## Activity Tracker
Seq | ID | Short Name | Description | Priority | Status
|  | *** OPEN ITEMS MIGRATED TO GITHUB ISSUES 2026-09-12 *** | Open tracking moved to github.com/skyemoor/VA-Energy-Plan-Input/issues on 2026-09-12. THIS FILE IS NOW AN ARCHIVE OF CLOSED ITEMS -- do not edit migrated rows here, edit the issue. Mapping: tracker 56->#1, 57->#2, 59->#3, 60->#4, 61->#5, 62->#6, 63->#7, 66->#8, 67->#9, 68->#10, 70->#11. Items 64, 65 and 69 were closed before migration and stay here only. Item 58 (gas merit order) was closed 2026-09-12 when the stack was wired in. Labels: scenario:N / common for scope, domain:X mirroring docs/INDEX.md, state (decision-needed, blocked, needs-data, in-progress) and kind (finding, defect, regression, research, deliverable). Priority is a milestone, not a label, so it sorts and shows progress. Commits close issues with "Fixes #N" -- which is the point: the work and the record stop being separate artifacts, the failure mode that let this sheet go un-updated for a whole session.
1 | 1 | Fix existing-solar bug | Correct the existing-solar generation input, currently modeled as a flat, round-the-clock output rather than real hour-by-hour solar generation. Confirmed to overstate existing solar's contribution by roughly 4x, causing every affected new-build figure to be understated. | 1 | c
2 | 2 | Fix CVOW wind bug | Correct the offshore wind (CVOW) generation input, currently scaled against an incorrect reference capacity (2,600 MW used vs. 2,535 MW confirmed nameplate) and normalized against its own observed peak rather than true nameplate. Confirmed to overstate CVOW output by roughly 20% in high-wind hours. | 1 | c
4 | 4 | Assumptions clean-up | Review the annual model spreadsheet for stale assumption values, input cells still marked in red/placeholder font that were never finalized, and known updates or corrections from prior conversations that have not yet been applied to the workbook. | 2 | C
3 | 14 | Capture assumptions that are only in code in the Assumptions tab | All explanations and reasoning that started out in the code need to be captured in the Appendices | 1 | C
5 | 15 | Exportable assumption question | “Exportable surplus share of solar-family generation” what is the need for this? Source? | 1 | C
6 | 16 | Distribution update cost references | “Distribution transformer gross upgrade cost” let’s look for substantive sourcing for this, especially from NY, CA, MA, MD. If there is not enough information from those states, see if other states have similar renewable energy targets or RPSs and include them in related information searches wrt solar, storage, transmission, distribution costs and other related information that we use in our modeling | 2 | ns
7 | 17 | Commercial/third-party-owned ITC (Section 48E) | Find out if there is an end/expiration date for this Commercial/third-party-owned ITC (Section 48E) | 1 | C
8 | 5 | Correct DER carve-out basis | Correct the distributed-solar (<=1MW) carve-out calculation, currently described as a direct percentage of total retail electricity sales. The statute defines it as a percentage of the RPS clean-energy requirement itself, which is a smaller, gradually-growing effective share of total sales. Update the affected REC revenue schedule accordingly. | 2 | C
9 | 6 | Re-check REC price estimates | Determine whether the third-party REC market price estimates (the projected revenue schedule) need revision given the carve-out basis correction in item 5, or whether only this project's explanation of the mechanism was wrong while the price estimates themselves remain valid. | 3 | C
10 | 7 | Evaluate interim milestones | Decide whether Scenario 2's buildout targets should reflect the statute's detailed interim milestones (specific MW thresholds at intermediate years) rather than the current simple straight-line ramp to each 2030/2035/2045 target. | 3 | C
11 | 8 | Farmland lease income analysis | Build the farmland lease income calculation for Virginia landowners hosting utility-scale solar, using researched lease rates ($1,200-2,500/acre/year in VA) and land-use factors (4-6 acres/MW for single-axis tracking) applied to corrected solar build sizes. | 2 | D1,2,3
| 9 | Ground locational value credit | Replace the out-of-state (New York) benchmark currently used for the locational value credit with a figure derived from Dominion-specific avoided transmission investment data. | 3 | D1,2,3
| 10 | Test additional ownership splits | Run the owner-economics model at ownership splits beyond the current 80/10/10 utility/rooftop/parking-lot baseline (e.g., 70/15/15, 60/20/20) to assess whether owner economics remain positive as the distributed-generation share increases. | 3 | D1,2,3
| 11 | Update appendix draft | Update the reorganized appendix draft with corrected figures throughout, reflecting the outputs of items 1-3 and any completed items among 4-10. | 2 | D1,2,3
| 18 | Agrivoltaics appendix add | Make an appendix for agrivoltaics | 1 | C
| 19 | reference VA Agrivoltaics code | Refer to VA code for agrivoltaics § 10.1-1197.5 | 1 | C
| 20 | # of farms in VA | Reference number of farms in VA | 1 | C
| 21 | acres of farmland in Virginia | Reference amount of farmland in Virginia | 1 | C
| 22 | loss of farms in Virginia | CORRECTED: per USDA/NASS "Farms and Land in Farms, 2025 Summary" (Feb 2026), Virginia lost 400 farm operations in 2025 (39,000 in 2024 to 38,600 in 2025) -- not the ~1,600 figure previously cited (source/scope of that earlier figure not independently reconciled). | 1 | C
| 23 | 90% agrivoltaics | Make an assumption that 90% of utility solar that will be categorized as agrivoltaics | 1 | C
| 24 | livestock and crops agrivoltaics | Identify types of livestock, hay, and crops that can be used with agrivoltaics with a focus on those that are suitable for Virginia | 2 | C
| 25 | Agrivoltaics placeholder in Exec summary | Put in placeholder for Mention of high level agrivoltaic benefits to VA farmers in exec summary | 1 | C
| 26 | battery acreage | Find out the acreage required for sodium ion and iron air storage, and if there are any projections about improved MW/MWh per square feet ‘footprint’ efficiencies. The iron air technology is so new that there will likely be significant ‘footprint’ efficiencies | 1 | C
| 27 | firmed solar acreage | Come up with an estimate of the amount of land required for utility storage that we can add to the 4-6 acres per MW of solar for utility solar. | 1 | C
28
| 3 | Recompute all scenario figures | Re-run every checkpoint solve and recompute build sizes, SLCOE, and all dependent figures across every scenario (1, 3, 1B, 3B, 2 and its gas-price tiers) using the corrected existing-solar and CVOW inputs from items 1 and 2. PROGRESS: Scenario1 ($39.03/MWh), Scenario1B ($37.60/MWh), Scenario2_Base ($46.85/MWh), and Scenario3 ($38.17/MWh) all fully re-solved (4 checkpoints each) and live in the workbook with corrected nuclear/exist_solar/wind/demand/gas-cost inputs. Remaining: Scenario2_Low, Scenario3B terminal checkpoint. Scenario3B now also complete ($33.81/MWh, the lowest of all six variants -- combines both DSM demand reduction and 5% gas terminal flexibility). Remaining: Scenario2_Low only. COMPLETE: all 6 scenario variants now fully re-solved and live: Scenario1 $39.03, Scenario1B $37.60, Scenario3 $38.17, Scenario3B $33.81, Scenario2_Base $46.85, Scenario2_Low $41.07/MWh. FULLY COMPLETE. CORRECTION: Scenario2_Low was found to already be correctly rebuilt (verified against fresh independent calculation, exact match) -- an earlier claim that it was still stale was wrong and has been corrected. Scenario2_High built from scratch (tab did not exist) using new gas_cost_mwh_hughes() function (Post Carbon Institute/Hughes 2021, $3.50->$11.50/MMBtu, compound-growth interpolation between the two sourced endpoints, explicitly caveated). COUNTERINTUITIVE, DOCUMENTED FINDING: High's PV-weighted SLCOE ($46.85/MWh) is virtually identical to Base's ($46.85/MWh) despite Hughes reaching $57/MWh by 2045 vs Deloitte's $44 -- because Hughes starts BELOW both other cases in 2026 and does not overtake Deloitte until 2035-2040, and PV discounting weights near-term years heavily. This is documented directly in the tab, not just here. ALL SIX scenario variants (1, 1B, 2 Base/Low/High, 3, 3B) now fully re-solved, live in the workbook, and internally consistent. Item 3 complete. | 1 | C
| 12 | Draft executive summary | Draft a non-technical, findings-first summary document for senior decision-makers, built on the finalized appendix content. | 4 | D11
| 13 | Draft technical summary | Draft a full-methodology-transparency summary document for technical reviewers, built on the finalized appendix content. | 4 | D11
Scenarios 1C/3C (variants of scenarios 1B/3B) where lowest possible SLCOE is optimized for final % clean vs. % gas
| 29 | Distribution avoided cost from load shifting | New assumption, kept separate from item 9 (locational value credit) for clarity: CPUC 2024 Avoided Cost Calculator Table 7-8 gives real $/kW-yr distribution capacity deferral values for PG&E/SCE/SDG&E, converting to $890-3,400/kW one-time equivalent (via our own CRF). This measures the benefit DERs provide by deferring capacity upgrades through load reduction -- distinct from item 16's transformer-upgrade cost (a burden DG triggers via reverse flow). CA-specific; VA/Dominion transferability and which distribution-constraint phase (near-term vs. long-term) applies to VA is unresolved. | 2 | ns
| 30 | Vintage-specific ITC modeling for DER NPV | DER Owner Economics tab currently uses a single, flat 2026-vintage ITC/MACRS benefit (15.2% rooftop, 38% parking-lot) for the NPV calculation, caveated as valid only for 2026-vintage projects. Section 48E ITC expires for new projects (no phase-down) after Dec 31, 2027 (general) or Dec 31, 2030 (safe-harbored, construction begun by Jul 4, 2026 -- deadline already passed). Build a fuller, vintage-specific version that correctly zeroes out the ITC benefit for projects built after the applicable deadline, rather than applying the 2026 rate uniformly across the full 2026-2045 analysis window. | 2 | C
| 31 | Fix Scenario 2 solar AND storage buildout to match statutory interim milestones | INPUTS PREPARED (scenario2_buildout_targets_2026_2045_v3_milestones.csv) -- 2030 checkpoint now correctly 10,000 MW solar/4,000 MW storage-short, matching statutory milestones. Replace Scenario 2's simple straight-line solar/wind ramp with the statute's actual, front-loaded interim milestones (6,000 MW by 2027, 10,000 MW by 2030, 16,100 MW by 2035). Current ramp understates the 2030 checkpoint by ~2,844 MW, likely overstating required CCGT capacity and gas cost at that checkpoint. Requires replacing the 2030 solar target and re-solving. ALSO: storage's 4,000 MW 'petitioned for by 2030' milestone, treated as installed capacity per user instruction (ours: 3,368 MW, gap ~632 MW) -- smaller than the solar gap but incorporated into the same fix/re-solve. | 2 | D3
| 32 | Fix flat gas cost, Scenario 1/3/1B/3B (RESTORED -- lost in tracker transition) | VERIFIED COMPLETE, 2026-09-03: checked directly against driver.py (not assumed) -- run_solve() and run_solve_multi_duration() both call lp.gas_cost_mwh(year, heat_rate=lp.SIMPLE_CYCLE_HEAT_RATE), the correct heat rate for Scenario 1/3/1B/3B/3C per the later heat-rate fix (item 49). This item's own originally-described target trajectory ($34.56/2030, $37.60/2035, $40.64/2040, $43.95/2044.5) is ITSELF STALE -- it was computed using the CCGT heat rate (6.4), superseded by item 49's correction to the simple-cycle heat rate (9.5) for these scenarios. The correct, current trajectory is $51.30/2030, $55.81/2035, $60.32/2040, $65.24/2044.5 -- confirmed by direct recomputation from gas_cost_mwh()'s own Deloitte $/MMBtu data points ({2026:3.70, 2030:5.40, 2040:6.35, 2050:7.50}) x SIMPLE_CYCLE_HEAT_RATE. The live Scenario3 tab's $38.17/MWh result (item 3) already uses this correct trajectory via driver.py -- no re-solve needed for this specific issue. Original task (replace flat $48/MWh with a time-varying trajectory) is complete; superseded by item 49's own heat-rate correction, which this item's own description never caught up to until now. | 1 | C
| 33 | derived values to files | all derived values needed for calculations to be captured in files, instead of being held in memory or code | 1 | C
| 34 | Update readme tab limitation 1 | README limitation 1 needs to be corrected to reflect our approach of focusing on hourly data and calculations | 1 | C
| 35 | average Hourly nuclear data by month from EIA | Use monthly nuclear generation levels from EIA for VA nuclear plants from 2022-2025 to arrive at an average hourly profile by month, captured in a file to use instead of one steady state value as we've been using APPLIED to hydro_year1_2016_17.npz: nuclear now a real, 12-value monthly profile (2,946-3,695 MW) instead of a flat 3,699 MW. Mean dropped to 3,280 MW. This INVALIDATES the already-solved 2030/2035/2040 Scenario 1 checkpoints (nuclear feeds every residual-demand calculation) -- user has confirmed these will be re-solved after item 36. | 1 | C
| 36 | Load demand projection DOM LSE | Change our load demand projections to align with Dominion Energy Virginia LSE projections per the link provided herein, though retain the information and citation about the growth rate projected by PJM of the DOM zone. https://apps.dlas.virginia.gov/User_db/frmView.aspx?ViewId=6885&s=7 APPLIED: two-component forecast built (1%/yr traditional load, isolated per JLARC/E3 sourcing; explicit 24/7 data-center addition ramping 3,583->9,000 MW by ~2034 per Dominions own 2024 IRP). Documented in Assumptions tab, derived_values_demand_forecast_v2.csv, and new Appendix_Load_Demand.md. Result: ~32% LOWER total demand by 2045 vs. old blended-rate approach. This further invalidates already-solved checkpoints -- confirmed pending re-solve alongside items 31/32/35. | 1 | C
| 37 | Investigate Bath pumped hydro underutilization | Sanity-check finding: Bath (existing, free, 3,000 MW/24,000 MWh) is active only ~271 of 8,760 hours (~3%) in the 2030 checkpoint solve, and shows ZERO activity in both the Jan 1-3 and Jul 1-3 windows checked -- even during Jul 1-3 when sodium-ion is actively, robustly cycling with abundant solar surplus available. Working hypothesis, NOT verified: sodium-ion's higher round-trip efficiency (90% vs Bath's 80%) may be "crowding out" Bath economically, with Bath only activating in a small number of the most extreme, highest-value hours where even sodium's large build is saturated. Next step if pursued: examine Bath's actual ~271 active hours directly to test this hypothesis. UPDATE: confirmed Bath IS fully modeled (own SoC dynamics, bounds), charge/discharge limit confirmed at exactly 3,000 MW. No explicit cycle-per-day constraint exists -- Bath's ~8-hour full-cycle time (24,000 MWh / 3,000 MW) is a physical consequence, not an enforced rule. Found an additional real constraint: year-end SoC is forced to equal year-start SoC. Working hypothesis strengthened (not yet fully proven): sodium-ion's better round-trip efficiency (90% vs Bath's 80%) may make it economically preferred for routine arbitrage, reserving Bath for rare, highest-value hours. PAUSED per user decision -- satisfied with this hypothesis for now, not pursuing further verification (e.g., examining actual active hours) at this time. | 3 | IP
| 38 | Code audit: values pulled from files vs. hardcoded/stale | COMPLETE. Verified derived_values_constants.csv and derived_values_by_year.csv still match live lp_model.py code exactly (0 mismatches). Searched all .py files for separate hardcoded copies of key constants -- none found. CRITICAL FINDING: the nuclear, exist_solar, and wind bug fixes (applied to hydro_year1_2016_17.npz much earlier this session) had NEVER been propagated to hydro_year2_2013_14.npz or hydro_year3_2012_13.npz -- the two weather years used for Phase 2 cross-testing/robustness verification. All three arrays were still flat/stale in both files. FIXED: applied the same corrections (real monthly nuclear profile; exist_solar x each files own solar_cf; wind x 2115.32/2535 rescale) to both files. Verified all three weather-year files now consistent. | 1 | C
| 39 | Relabel scenario tabs, remove _HourlyRPS suffix | COMPLETE. Backup created (VA_SLCOE_Model_BACKUP_pre_tab_rename_2026-08-11.xlsx) before any changes. CRITICAL FINDING during safety check: old, superseded Scenario1B/Scenario3B tabs (pre-correction, flat-5%-throughout interpretation, still referencing the deleted annual-model tabs in their own text) still existed alongside the correct _HourlyRPS versions, and Summary!B27/B28 were actively pulling from the STALE ones -- showing 1.81/MWh and 9.34/MWh vs. the correct 8.30/6.53 (a real ~12% overstatement, not just a labeling issue). FIXED: repointed Summary to correct tabs, verified zero other references, deleted the two superseded tabs, then renamed all four _HourlyRPS tabs (Scenario1, Scenario3, Scenario1B, Scenario3B), updated the 2 formula references and 8 descriptive text mentions of the old suffix. Verified zero remaining references anywhere in the workbook. | 1 | C
| 40 | Sweep stale $33.15/MWh Scenario1 SLCOE references | Scenario1 SLCOE updated from stale $33.15/MWh to corrected $39.03/MWh (per item 3 re-solve with corrected nuclear/demand/gas-cost inputs). Old figure still referenced in: Scenario1s own methodology-note text and comparison line (row 54), plus cross-references in Scenario3, Scenario2_Base, Scenario3B, and (once built) Scenario1B. Sweep all instances to the corrected figure once identified. Note: this is separate from the tab-relabeling text sweep (item 39), which fixed naming/suffix references but not dollar figures. COMPLETE. Fixed all 4 cross-references (Scenario3, Scenario2_Base, Scenario3B, Scenario1B) to $39.03/MWh. Also fixed: Scenario1s own gap claim (recomputed $51.67 vs old-model gap from ~36% to correct ~24.5%), and Scenario1Bs stale gas-percentage text (46.34/33.79/17.40% -> corrected 59/41/21%). Also caught and fixed a _HourlyRPS suffix that had been reintroduced into Scenario1B!A51 as a side effect of the wholesale backup-restore used to fix the earlier row-corruption error. Verified zero remaining instances of old figures workbook-wide. | 1 | C
| 41 | VPP revenue for firmed (solar+storage) DER owners | CONFIRMED: solar-only DER excluded from VPP participation (Dominion pilot explicitly excludes solar-only, already compensated via net metering). Researched comparable VPP rates across multiple states/programs (ConnectedSolutions family: MA/RI/CT/NH/ME, capacity-based $/kW; California: DSGS/ELRP/SMUD, energy-based $/kWh or enrollment bonuses). Added new VPP revenue section to DER_Owner_Economics tab for firmed (solar+storage) systems: $200/kW-summer + $100/kW-winter, matching NH ConnectedSolutions structure specifically, chosen for its stronger winter weighting given VA data-center-driven winter peak (this projects own judgment, not independently sourced). Battery-to-solar pairing ratio (1.0 kW/kW-AC) is an explicit, separate, clearly-flagged assumption, not a sourced standard. NOT yet incorporated into Section H/J NPV calculations -- standalone estimate pending decision on integration. | 2 | IP
| 42 | Fix Scenario3B 2041-2044 interpolation bug (user-caught) | USER CAUGHT: Scenario3B solar/CCGT/cost figures diverged from Scenario3 starting 2041, despite both scenarios sharing an identical trajectory through 2044 (only 2045 should differ). ROOT CAUSE: when building 3B, the 2040-2045 segment was freshly piecewise-interpolated using 3Bs own, lower 2045 endpoint -- pulling 2041-2044 down too. 1B did NOT have this bug, since its 2026-2044 rows were built by directly copying Scenario1s already-computed values, not re-interpolating. FIXED: directly copied Scenario3 rows 19-37 (2026-2044) into Scenario3B rows 26-44, matching 1Bs correct method. RESULT: Scenario3B SLCOE corrected from $33.81/MWh to $36.80/MWh (~8.8% increase, since the bug had understated 2041-2044 costs). No other workbook references to the old figure were found needing cleanup. | 1 | C
| 43 | Build Scenario 3C -- unconstrained, cost-optimized gas/clean mix | NEW scenario, revives the orphaned 1C/3C idea from item 33. Built on Scenario 3s DSM demand, with the RPS gas-share constraint removed entirely and gas-sourced export disabled. Key assumption, explicitly disclosed: gas dispatch carries zero CAPEX (existing Dominion LSE turbines treated as sunk, per user confirmation) -- favors gas heavily, does not claim gas is fundamentally cheaper than solar. RESULT (all 4 checkpoints, consistent): zero new solar/storage ever cost-justified; gas share ~83-87% of non-nuclear demand. SLCOE = $23.45/MWh -- substantially below every RPS-constrained scenario, quantifying the direct cost of the RPS policy constraint itself under this assumption. FLAGGED FOR FUTURE WORK: end-of-life replacement of existing gas turbines during 2026-2045 is not modeled and may require revisiting this assumption for later years. A social-cost-of-carbon version of this optimization (Scenario 3C-SCC or similar) was discussed as a natural follow-up but not yet built. MAJOR CORRECTION: original unconstrained-gas version (SLCOE=$23.45/MWh) found to be self-contradictory -- implied gas capacity (13,966-17,429 MW peak) far exceeded any real existing fleet while claiming zero CAPEX. User-directed research identified and data-verified (via each plants own EIA generation history, not just secondary sources) 7 existing gas plants totaling 7,747.6 MW nameplate. Applied user-selected 30-year CCGT lifespan (cycling-driven thermal stress). Retirement schedule validated against actual generation data: Gordonsville data stops Dec 2024 (consistent with formula-predicted retirement); Chesterfields formula-predicted 2020 retirement contradicted by data (still generating through May 2026), held operating through full window instead of forcing unsourced date. Time-varying capacity cap applied: 7,447.6 MW (2026-2030) -> 6,472.6 MW (2035-2040) -> 4,410.6 MW (2045). CORRECTED RESULT: substantial new solar/storage now cost-justified (unlike original zero-build result). SLCOE = $53.11/MWh -- REVERSED from lowest to HIGHEST of all six scenarios. Genuine finding: unguided, capacity-constrained optimization without RPS structure can be MORE expensive than policy-driven scenarios, not automatically cheaper. | 2 | C
| 44 | Precisely determine Chesterfields current active gas capacity | USER CAUGHT: Chesterfields max monthly output dropped substantially starting ~2016-2019 (992,984 MWh in 2016 -> 540,742 in 2019 -> 255,190-324,976 in 2023-2025), suggesting most of the original 1,446.6 MW nameplate fleet has retired, not just one unit. Rough 30-day-month approximation implies only ~350-450 MW currently active (2023-2026) -- a ~70% reduction from the nameplate figure used throughout Schedule A and the Scenario 3C gas-capacity cap. NEEDS: (1) exact days-in-month calculation (not 30-day approximation) for precise current capacity, (2) identify specific month(s) of step-change(s) to pin down timing, (3) propagate corrected figure through Schedule A and re-assess Scenario 3C (likely pushes SLCOE higher still, since less gas capacity means more required new solar/storage). ALTERNATIVE HYPOTHESIS TO INVESTIGATE (user): declining output may reflect RESERVE/standby status, not physical retirement -- units still available but dispatched less often as newer, more efficient CCGT capacity (Warren County 2014, Brunswick County 2016, Greensville 2018) came online and took over via merit-order economics. Timing lines up well: these three plants online almost exactly when Chesterfields output began declining (2016-2019). If true, the correct capacity figure for our gas-constraint purposes (physically AVAILABLE capacity, not historical dispatch level) could still be close to the full 1,446.6 MW nameplate, not the ~350-450 MW implied by recent utilization -- these represent two different things (availability vs. actual recent merit-order dispatch) and should not be conflated. Needs investigation: whether Chesterfields older units have been formally deactivated/mothballed vs. simply run less. | 2 | ns
| 45 | Peaker plant data confirmation (group b, high-priority 4) | RESOLVED, high-priority 4 of 10 peaker/mixed-type plants: Gravel Neck, Elizabeth River, and Darbytown all CONFIRMED RETIRED (generation stops Dec 2024, identical pattern to Gordonsville, 0/12 active months in most recent year) -- validates our earlier conservative assumption. Doswell CONFIRMED STILL OPERATING (12/12 active months through May 2026, same pattern as Chesterfield) -- formula-predicted 2021 retirement contradicted. Doswell capacity refined to ~901 MW (data-derived from peak output) vs. earlier 752-1313 MW secondary-source range. Doswell EOH=96,606, near top of mid-life overhaul window. Schedule A/B capacity totals updated accordingly (net effect: +901 MW throughout window from Doswell addition). REMAINING: 6 lower-priority peaker plants still need data (Remington, Ladysmith, Wolf Hills, Louisa, Possum Point, Marsh Run) -- all have formula retirement still in the future, so lower urgency. UPDATE: remaining 5 lower-priority plants now also confirmed. Remington, Marsh Run, Louisa ALL confirmed RETIRED (same Dec-2024-cutoff pattern as the earlier 4) -- retired earlier than their own 30-year formula dates, at low EOH (11,000-16,000), suggesting economic not physical retirement. Possum Point and Ladysmith confirmed STILL OPERATING. Notable: Possum Point EOH=127,214, far above the mid-life window -- heavily utilized despite peaker classification, unlike Ladysmith (EOH=16,718, genuine low-utilization peaker profile). Wolf Hills remains unconfirmed (no data uploaded). Seven total plants now show the identical Dec-2024 retirement cutoff across two different owners -- flagged as worth independent verification, not yet done. Full capacity schedule recomputed: 9,647 MW at 2026 (down from 11,341), declining to 5,634 MW by 2045. Peaker plant data collection essentially complete (9 of 10 plants now have direct generation-data confirmation). FINAL UPDATE: Wolf Hills data now received and processed -- 10/10 peaker plants have direct generation-data confirmation. Wolf Hills shows the same zero-output-since-Dec-2024 pattern as 7 other plants (now 8 of 10 total, cause unconfirmed per item 47s independent verification finding). Final capacity schedule: 9,362 MW at 2026 (down from 9,647), declining to 5,634 MW by 2045. Peaker plant data collection is now fully complete. | 2 | C
| 46 | Rebuild gas plant master file using authoritative SEC data | MAJOR CORRECTION. Found Dominions own official SEC 2023 Form ARS filing with exact Net Summer Capability for nearly every Dominion-owned gas plant -- used as primary source, superseding secondary-source figures throughout. KEY FINDING: Chesterfields true gas-only capacity (Units 7&8) is 386 MW, not the 1,446.6 MW used throughout this project -- that figure was the combined coal+gas total of the original 8-unit site. Chesterfields observed 2016-2019+ output decline was entirely due to COAL unit retirements (Units 3&4 March 2019, Units 5&6 May 2023), confirmed directly by Dominion spokesperson: gas Units 7&8 explicitly still in service. Chesterfields EOH calculation is therefore INVALID (mixed coal+gas generation divided by wrong capacity) -- needs recompute using post-June-2023 gas-only data, not yet done. TWO NEW PLANTS IDENTIFIED: Bremo (227 MW) and Bellemeade (267 MW), both confirmed retired March 2019 as part of an official, SEC-confirmed six facilities/1,292 MW cold-reserve retirement round (2 of 6 facilities still unidentified by name). CERC APPROVAL STATUS CORRECTED: was reported as approved, actually SUSPENDED after community pushback (Dec 2025) -- do not treat as confirmed. Full capacity schedule recomputed: 11,341/10,722/7,032/7,032/5,061 MW at 2026/2030/2035/2040/2045 (down from the prior, less-authoritative 12,713.6/12,007.6/8,166.6/8,166.6/6,104.6 MW schedule). | 3 | IP
| 47 | Chesterfield gas-only EOH recompute + retirement pattern verification | TASK 1 COMPLETE: Chesterfield gas-only EOH computed using confirmed post-June-2023 window (coal Units 5&6 retired May 31 2023): 16,487 EOH over 36 months, 62.7% capacity factor. Extrapolated full-history estimate: 137,000-198,000 EOH depending on start-year assumption -- well above the mid-life window, though extrapolation is directional only (assumes constant utilization, which is unlikely given coal units previously carried most baseload). TASK 2 INCONCLUSIVE, HONEST FINDING: independent verification search for the seven-plant Dec-2024 retirement pattern found NO direct news/regulatory confirmation. Third-party databases found (gridinfo.com, GEM) share the same underlying EIA data and cutoff -- not independent. GEM still lists Gordonsville as operating status (Jan 2026). REVISED all 7 plants master-file language from CONFIRMED RETIRED to zero-output-since-Dec-2024, cause unconfirmed -- treated conservatively (excluded from capacity) but explicitly flagged as uncertain, not confirmed fact. BONUS FINDING: CERC approval status corrected again -- SCC reasserted approval after declining to reconsider (was reported as suspended in an earlier finding this session); current status is approved, though facing a separate air-permit appeal. Also found alternate CERC figures (944 MW, not 1,000; 33% capacity factor) worth noting. | 2 | C
| 48 | Overhaul/retain assumption established as leading option for gas shortfalls | Scenario 1 dual-constraint (RPS % + Schedule B capacity cap) solved for 2030/2035/2040: only 2035 shows a genuine capacity shortfall (existing 7,605 MW fleet maxes out at ~27.2% gas share vs 41% RPS-allowed ceiling; 2030 and 2040 both converge within existing capacity). Additional capacity needed at 2035: ~1,721-1,777 MW. THREE-WAY NPV COMPARISON computed: Option 1 (no action, over-comply via extra solar/storage) PV=$92,742.7M; Option 2 (new-build ~1,777 MW simple-cycle, stranded-basis 10-yr capital recovery since worthless by 2045) PV=$89,525.9M; Option 3 (overhaul/retain Tenaska Virginia [975MW, ~$22.5M overhaul] + Ladysmith [782MW, no capital work needed per low EOH]) PV=$88,048.8M -- CHEAPEST by $1,477.0M vs new-build and $4,693.9M vs no-action. ESTABLISHED AS LEADING ASSUMPTION, explicitly caveated as unconfirmed (overhaul cost is a midpoint estimate; Ladysmiths no-capital-work conclusion is inferred not confirmed; Tenaska Virginia is third-party owned, requiring a negotiated retention agreement). Reference files updated: new_peaker_ccgt_costs_by_size.md (leading-option section added above the new-build standing rule) and VA_gas_capacity_schedules.md (Schedule A recomputed with both plants retained through 2040: 9,362 MW flat 2026-2040, vs previous declining schedule). Master plant file updated with per-plant assumption notes. PRACTICAL RULE established: future shortfalls should first check for near-EOL plants at that checkpoint before defaulting to new-build. | 3 | IP
| 49 | Build View #1 for 5 identified low-output windows | Built loudoun_battery_dispatch.py hour-by-hour battery dispatch simulation (100-hr/80% RTE, 1,551.2 MW), then View #1 stacked-bar+line combo charts (Graphical Views tab definition) for the 5 windows found earlier via the Sterling solar low-output streak analysis: Feb 2018 (75hr), Sep 2018 (71hr), Dec 2018 (71hr), Nov/Dec 2015 (69hr), Jan 2013 (68hr), each +/- 1 week. Nuclear/wind omitted (not modeled in this Loudoun-specific analysis, stated explicitly on each chart, not fabricated). Finding: in all 5 windows, solar never once exceeds the ~90%-of-peak flat worst-case load, so the battery never recharges once depleted -- SoC drops from 100% to 0% within the first ~140 hours of every window and stays there. Real bug caught and fixed during this build: an initial ~19x load/solar scale mismatch (comparing real Dominion-zone absolute MW load against the Loudoun-specific canopy fleet) produced a misleadingly small ~1.4% difference between battery durations, corrected to load = load_pct_of_peak x solar fleet MW -- see Data_Sourcing_Log.md. | 1 | C
| 50 | Add curtailment to View #1 dispatch simulation | Follow-up to item 49. After merging into the real uploaded tracker file, pulled the real View #1 spec text directly from it (rather than the earlier transcript-reconstructed version) and found it had evolved: adds 'gas' to the positive stack (omitted here, same reasoning as nuclear/wind -- not modeled in this Loudoun-specific analysis) and 'hourly curtailment (replaces export, which no longer exists in the corrected no-export model) as a negative bar alongside battery charging' -- a real, previously-untracked dispatch output. Added curtailment_mw to loudoun_battery_dispatch.py's simulate() (excess solar the battery couldn't absorb: excess - charge_mw), plus a new, stronger Rule 9 invariant verifying the full hourly energy balance closes (solar+discharge+residual_import == load+charge+curtailment) every hour, not just curtailment non-negativity alone. All 5 View1_* sheets rebuilt with curtailment as a negative bar. Finding: curtailment is exactly zero in all 5 windows, consistent with the already-established finding that solar never exceeds the worst-case flat load in any of them. | 1 | C
| 51 | Prince William C&I rooftop + parking-lot assessment | C&I: 2,497 real buildings >=600 sqft (922.2 acres) from user-provided PWCCommericialBuildings.xlsx -> 272.8 MW / 477,985 MWh/yr (mean-based). No industrial code in PWC's own StructureType schema (confirmed against full legend) -- likely folded into "3=Commercial," composition not directly comparable to Fairfax/Arlington's narrower categories. No dedup field exists in this dataset (OBJECTID/GlobalID both confirmed fully unique) -- open limitation, not resolved. Parking lots: direct PWC GIS extraction failed (TYPE_CODE field returning zero results) -- built a density-based ESTIMATE instead (not measured), Loudoun-anchored per-capita, per direct user decision (PWC's greater distance from DC vs. Fairfax implies less structured/garage parking, more surface-lot, similar to Loudoun's own pattern) -> 1,734.7-2,168.4 MW / 3,039,279-3,799,098 MWh/yr. Fairfax-anchored figure (162.4-203.0 MW) retained as an explicit sensitivity check, not blended in. Schools (theoretical potential, already existed in shared module): 35.05 MW / 140,200 kWh. New modules: prince_william_ci_rooftop_solar_estimate.py (11 tests), prince_william_parking_lot_density_estimate.py (12 tests). | 2 | C
| 52 | Northern Virginia solar assessment -- four-county consolidation | Merged Loudoun-only and Fairfax/Arlington-only assessment docs plus new Prince William section into one Northern_Virginia_Solar_Assessment_Methodology_and_Findings.md (superseding both prior docs, both archived). Restructured executive summary per direct user request: grand total table -> by-asset-type table -> by-county table, preceded by a new executive-level intro paragraph (prior "combines and supersedes" provenance note removed). Grand total, all four counties, all components: 6,159.0-7,148.2 MW / 10,790,592-12,523,613 MWh/yr. Cross-county comparison and consolidated limitations sections (12 items) expanded to fold in Prince William-specific findings. | 2 | C
| 53 | Loudoun County data center address inventory | Compiled 246 data-center facility records (operator, address, source) across multiple named operators (Digital Realty, Equinix, NTT, Vantage, CyrusOne, AWS, Microsoft, QTS, Aligned, Google, STACK) plus Loudoun County's own official GIS land-use extract (223 records, "COM_DATA_CENTER" classification) -- initially misjudged as stale (Nov. 2020 layer-metadata label) but verified directly against the extract's own year-built/permit-date fields to be genuinely current through ~mid-2025 (user caught the initial, incorrect staleness assessment). 60 of 246 rows have a confirmed named operator; 186 remain "Unknown (public permit record)," not yet resolved. CSV: loudoun_data_centers.csv. STATUS: in process -- operator resolution for the remaining 186 rows not complete (T5, Compass, Iron Mountain, Rackspace not yet checked). | 3 | IP
| 54 | Text-file reorganization & debugging-log consolidation | Archived 10 confirmed-superseded text files (each verified via direct diff/content comparison, not assumed) to a new archive/ subfolder: capitalized Software_Engineering_Standards.md duplicate; Solve_Procedure_and_Requirements.md and Appendix_P_Working_Draft.md (both confirmed strictly superseded by Appendix P's own copy in Reorganized_Appendices_Draft.md via 3-way diff); Dominion_VPP_Pilot_Research.md and ThirdParty_VPP_DERA_Compensation_Benchmarks.md (superseded by DERA_VPP_WMA_Consolidated_Working_Notes.md); Loudoun-only and Fairfax/Arlington-only solar docs; both loudoun_test_batch raw-notes files; Appendix_Scenario3_Main_DRAFT.md. Completed a full, 133-entry (125 numbered + decimal sub-entries) read-through of Internal_Debugging_Log.md -- title-based triage proved unreliable (two suspected-routine entries turned out substantive on full read); extracted 3 named, recurring mistake patterns into Common_Mistake_Log.md instead of a bulk migration (str_replace header-consuming edits, 6 occurrences; silent block-misplacement; case-only-different-filenames, confirmed recurring via 2 independent instances). Resolved and closed the debugging log's own long-standing "open question" note. STATUS: in process -- the actual appendix merge (A-F from _updated, M-P from the original) and the broader tiered file-placement pass remain open. | 3 | IP
| 55 | REC banking + deficiency-payment tradeoff model | REC banking under Va. Code 56-585.5(C)(4), implemented as a BEHAVIORAL model (design decision #3 of three options considered, chosen 2026-09-10): the trajectory should model the utility's own economic CHOICE between banking surplus RECs and paying the 56-585.5(D)(5) deficiency payment, not merely report compliance accounting given a fixed build. PURPOSE: identify where the deficiency-payment ceiling ($45/MWh base, escalating 1%/yr, reaching ~$57/MWh by 2045) becomes a weakness in the compliance regime -- i.e. the point at which paying the deficiency is cheaper than building, given both higher gas prices and the very high clean-energy costs the 100% pathway implies (2045 physical SLCOE modeled near $133/MWh, provisional). DESIGN (drafted, not built): new RECBank class holding vintaged balances -- a REC of vintage Y is valid in Y through Y+5, a six-year window; deposit, retire FIFO (oldest first, since those expire soonest), expire AFTER retirement (vintage Y remains valid THROUGH Y+5). New MultiYearComplianceTrajectory class sequences years and owns the bank. Existing single-year classes (StatutoryComplianceBase, StatutoryRPSObligation in lp_package/rps_compliance.py) remain unchanged and are used inside the trajectory. OPEN QUESTION carried forward: whether the 56-585.5(C)(2) distributed carve-out and 56-585.5(C)(1)(b) geothermal carve-out bank in SEPARATE vintage pools. The statute's banking language is general and arguably ambiguous; the conservative reading (separate pools, so an ordinary-REC surplus cannot satisfy a future carve-out) is recommended for a regulatory audience. LIMITATION to state when reporting: this is post-processing and retrospective. It reports what a utility would rationally do given a build path; it does NOT find the cheapest build path that exploits banking. That requires the multi-year coupled optimization tracked separately. | 2 | NS
| 56 | [-> GitHub #1] Flat hourly energy dual — MEASURED AT 2030 ONLY, causation corrected | MEASURED 2026-09-11 at 2030: the LP's hourly energy-balance dual has ONE unique value across all 8,760 hours (\$54.70/MWh). CAUSATION CORRECTED same day after challenge: this is NOT storage arbitraging prices to equilibrium. Storage carries a real cycling cost (\$5.43/MWh Na-ion, \$18.03/MWh iron-air, applied per discharged MWh in the objective), so it CANNOT flatten prices below that spread plus round-trip losses. The actual cause is that 2030 has ZERO curtailment and ZERO unserved energy, so gas is marginal in every hour -- and there is only ONE gas price. Storage sat idle because there was nothing to arbitrage. The earlier causation ran backwards. SCOPE CORRECTED: measured at 2030 only, then documented as model-wide. 2045 has ~42% of hours in net surplus (3,722 of 8,760, net load reaching -160 GW against a 22 GW peak); those hours must price at or near curtailment cost, so the 2045 dual SHOULD vary and the flat-dual finding may not hold there. THE 2045 SOLVE WAS ATTEMPTED THREE TIMES AND DID NOT COMPLETE -- it exceeds the available execution window (~253s solve plus overhead; killed at 295s foreground and again in background). Verifying the 2045 dual is the blocking next step before any claim about model-wide price behaviour. The single-gas-price cause is real in every year regardless. | 1 | IP
| 57 | [-> GitHub #2] all_hours_reserve.py exists but is never called | Weather_Year_Robustness_Approaches_and_Findings_2026-08-23.md documents three reserve-enforcement approaches and names 1c (LP-integrated, all-hours) as CURRENT STANDARD. lp_package/all_hours_reserve.py implements it -- itself rebuilt in a later session after the original chained_dispatch_test.py was lost. NOTHING CALLS IT. The only reference outside the module is a comment in driver.py. Every solve therefore uses approach 1a, the single-peak-hour constraint the same document calls the weakest of the three. HIGHEST-VALUE FIX AVAILABLE: the code exists, is documented, and was validated once. CAUTION FOUND 2026-09-11: it enforces availability in every hour, which is a HARD FLOOR -- stricter than any real reserve product. Contingency reserve is drawable under declared EEA-2/3; planning margin is probabilistic not hourly; PJM's day-ahead scheduling reserve explicitly covers load forecast error. Check whether the implementation permits drawdown or will force overbuild. | 1 | NS
| 58 | Gas merit order — fully sourced, ready to wire in | Heat rate tiers from EIA Electric Power Annual Table 8.2 (Form EIA-860, capacity-weighted, 2024): Combined Cycle 7,548; Gas Turbine 10,999; Steam 10,337. Five-rung stack spans 1.72x. CAPACITY PER RUNG RESOLVED 2026-09-12 from EIA-860 Schedule 3 (Generator Data), Virginia, Operable, NG, Virginia Electric & Power Co, rungs by per-unit Operating Year: ccgt_modern 4,717.7 MW (12 units, 2014+), ccgt_fleet 1,172.0 (6 units, 2000-2013), ccgt_legacy 747.0 (8 units, pre-2000), ct_fleet 2,722.8 (20 units); total 9,359.5 MW nameplate, reconciling exactly. BOTH PRIOR BLOCKERS CLEARED. (1) The CT aero/frame split is settled as ENTIRELY FRAME, from per-unit nameplate rather than inference: Ladysmith 5x178.5, Remington 4x170-178.5, Elizabeth River 3x129.6, Gravel Neck 4x91.9, Darbytown 4x92.1; aeroderivatives are 36-54 MW and not one Dominion unit is in that class. Statewide 91.9% of VA simple-cycle is frame. (2) The 1,167 MW discrepancy was NOT missing capacity -- it was NET SUMMER CAPABILITY (10-K, 8,195) versus NAMEPLATE (EIA-860, 9,359.5), ratio 87.6%, a normal derate. Schedule A's 9,362 agrees with nameplate to 2.5 MW. Two wrong hypotheses (IPP capacity, then ODEC capacity) were offered before the units were checked; both rating bases are now retained as separately named constants so the error cannot repeat silently. NEXT: wire the stack into the LP objective and dispatch, then re-extract hourly duals. This is the fix most likely to give the flat dual (ID 56) structure. RAISED TO PRIORITY 1 on 2026-09-12. Previously P2 on the reading that a merit order 'adds realism'. That understated it: the merit order is THE MECHANISM by which any intraday price structure can exist at all. Gas OUTPUT already varies enormously across the day -- less gas burned at midday when solar is producing, more in the evening, and wind variation moving dispatch throughout -- but with a SINGLE gas price, the marginal cost of one more MWh is the same at every output level, so none of that physical variation reaches the dual. The LP dual is MARGINAL cost, not average, and gas is on the margin in every hour at 2030. With five rungs, midday clears at ccgt_modern \$34.56 and the evening peak reaches ct_fleet \$59.39 -- roughly a \$25/MWh intraday spread from gas alone, before any scarcity pricing. Storage then has something to arbitrage, and its cycling cost sets a floor on how far it closes the spread. UNBLOCKS 56, 61, 68. WIRED IN 2026-09-12. build_problem(gas_merit_order=..., gas_merit_order_year=...), default OFF so prior behaviour is reproduced exactly. AT 2030 THE DUAL GOES FROM 1 UNIQUE VALUE TO 40, range \$37.56-3,690.71, std 215.15, minimum exactly ccgt_modern's marginal cost. Rungs dispatch in merit order: ccgt_modern 8,648 hours, ccgt_fleet 7,921, ccgt_legacy 6,396, ct_fleet 4,804. ADDITIVE DESIGN: IDX['g'] stays the hourly total so the energy balance, gascum and the gas-share constraint are untouched; per-rung variables are appended and tied by one equality per hour. Two bugs found and fixed during integration -- 'row' is SHARED between equality and inequality constraints in build_problem so it is not the equality row count (len(eq_rhs) is), and eqlin marginals come back POSITIVE, so an earlier measurement reporting the flat dual as -\$54.70 had the sign inverted. NEXT: measure 2045, which could not be solved in the session environment. | 1 | C
| 59 | [-> GitHub #3] No import capability in the model | export exists (capped, earning export_price_mwh); 'import' has ZERO occurrences. Virginia is modelled as an island that can sell into PJM but never buy. Dominion imports substantially in reality, so this likely OVERBUILDS -- inflating capacity in every scenario including the Utility Preferred Plan comparison. The honest middle is that imports are available EXCEPT during regionally correlated scarcity, which is exactly the dunkelflaute hours that drive the build. OPEN STATUTORY QUESTION: if the model imports PJM energy during scarcity, that energy is largely fossil -- whether it counts against 56-585.5, or whether REC-and-retail-sales accounting makes imports invisible, has real consequences for how much must be built. Deferred by user decision as its own work set, after the merit order and reserve work. SCOPE REDUCED 2026-09-12: under LMP an importer pays ITS OWN node's price, not the exporter's. So modelling imports does NOT require modelling PJM's supply stack -- it requires a price at the DOM node, and that price already embeds regional scarcity and congestion because that is what an LMP is. This makes the import question and the scarcity-pricing question THE SAME QUESTION, and removes the earlier objection that imports would collapse the build: imports priced at DOM LMP during a regional dunkelflaute are expensive by construction. The remaining independent constraint is the TRANSFER LIMIT into the zone, which is physical rather than economic. | 2 | DN
| 60 | [-> GitHub #4] Nodal price zones + weather-driven hourly prices | PJM requires energy-market aggregations at a SINGLE pricing node (capacity and ancillary may aggregate across nodes; energy may not) -- see DERA_VPP_WMA_Consolidated_Working_Notes.md section 4. The model treats the whole distributed fleet as one block against one price series, which energy-market rules do not permit. PROPOSED: zone into NoVA (Ashburn anchor, ~$28 floor), Richmond metro, SE Tidewater, and possibly a rural/southside set (NDOSWLDP, ~$6.89 floor -- whose low floor IS the congestion, and is the transmission-deferral argument in data). SECOND HALF: the project already holds hourly insolation and temperature for these locations, which in principle allow month-hour average prices to be varied down to individual hours of specific days -- addressing the finding that month-hour averaging removes 94.5% of the real extreme and the top 1% of hours hold 29.4% of positive congestion value. OPEN: whether either is tractable in the LP. Zoning multiplies the distributed variable set; weather-conditioned prices add a possibly non-linear mapping. The 2045 checkpoint already takes ~253s. INVESTIGATE BEFORE BUILDING. | 2 | NS
| 61 | [-> GitHub #5] Foresight bracketing implemented for S3 arbitrage value | lp_package/foresight_bracket.py bounds distributed storage arbitrage between a no-lookahead lower bound and a perfect-foresight upper bound, rather than a point estimate. Adopted because it introduces NO NEW PARAMETER -- no capacity reference, no price-response curve, nothing for a reviewer to name as arbitrary. Precedent: Brattle 'Stacked Benefits' (16% gap, regulatory valuation), Hornek et al. arXiv 2501.07121 (11%), arXiv 2505.12538 (LDES capacity expansion), arXiv 2407.21409 (96-hour rolling horizon, supporting 4-5 day horizons as within forecast skill). SCOPE ENFORCED: bounds ARBITRAGE VALUE ONLY, not reliability contribution -- Shen/Ilic/Parsons arXiv 2607.27021 show uncertainty induces a PRECAUTIONARY policy qualitatively different from degraded perfect foresight, so perfect foresight may not be a ceiling on reliability. STATUS: built and tested, not yet run against a real S3 solve. Blocked in practice by ID 56 -- the price series it brackets has no scarcity in it. | 2 | IP
| 62 | [-> GitHub #6] Capacity accreditation under precautionary operation | DEFERRED by user decision. capacity_accreditation.py carries 100.0% (LP dispatch, perfect foresight) and 31.8% (no-foresight heuristic) for 2045 storage, and the project treats 31.8% as the conservative usable figure. Shen/Ilic/Parsons (arXiv 2607.27021) complicate that: demand uncertainty induces a PRECAUTIONARY storage policy hedging against scarcity that may not arrive, which is qualitatively different from a degraded perfect foresight. A precautionary operator may hold MORE charge into peak hours than either the LP or a naive heuristic -- in which case BOTH existing figures sit below a realistic operator's contribution, and this project has been conservative in a direction it did not intend. Would require implementing a precautionary dispatch policy and comparing against both existing bases. | 3 | NS
| 63 | [-> GitHub #7] Documentation index by domain | docs/INDEX.md created 2026-09-11 after two collisions in one session: a gas fleet note written without checking docs/research/ (which already held a gas turbine lifespans reference), and an extended wholesale-market-arbitrage discussion conducted without consulting DERA_VPP_WMA_Consolidated_Working_Notes.md (which had already resolved several of the questions being asked). 54 markdown files across four subdirectories, previously unindexed. Organises by DOMAIN rather than folder, marks a START HERE entry point per domain, flags five fragmented domains. Gas domain wired hub-and-spoke (7 files, all pointing at Gas_Fleet_Working_Notes.md). test_docs_index.py asserts every markdown file appears in the index, so a new unlisted file fails the build. REMAINING CONSOLIDATION: Scenario 3 (381 KB, Scope_and_Gaps alone is 246 KB and likely holds resolved items). | 3 | IP
| 64 | Reserves approach — decision and reader summary | DECISION 2026-09-11: do NOT model contingency reserve. Rationale: NERC BAL-002 contingency reserve is sized to the Most Severe Single Contingency and the obligation belongs to PJM as Balancing Authority and Reserve Sharing Group -- met jointly across members, unaffected by the FRR/RPM election (which governs capacity procurement, not operating reserve). Requiring a Virginia-standalone model to self-provide full MSSC would impose on one zone what the region meets collectively. TWO CAVEATS RECORDED IN THE SUMMARY, both against the decision's favour: (1) sharing is ALLOCATION not EXEMPTION -- members contribute a share, so 'less than full MSSC' is defensible while 'none' is the opposite simplification, making capacity slightly cheaper than reality; (2) contingency reserve is not the only reason to hold hourly headroom -- BAL-002 covers outages, not renewable forecast error or net-load ramps, and PJM's day-ahead scheduling reserve (explicitly sized for under-forecasted load) is also unmodelled. CONSEQUENCE: no operating reserve is active in any hour, so storage discharges to its floor in all 8,760 hours, which is the mechanism behind the flat hourly dual (ID 56). Dropping the constraint removes the rationale for wiring in all_hours_reserve.py (ID 57) -- those two items are now coupled and should be decided together. Reader-facing summary written: docs/methodology/Reserves_Approach.md, stating the net effect as CONSERVATIVE ON CAPACITY and PERMISSIVE ON OPERATIONS, so capacity results are usable while hourly price, arbitrage and scarcity results are not. | 1 | C
| 65 | Documented fixes regressing — process risk | TWO INSTANCES FOUND 2026-09-11, both discovered by reading code rather than documentation. (1) all_hours_reserve.py implements the LP-integrated all-hours reserve constraint that Weather_Year_Robustness_Approaches_and_Findings_2026-08-23.md names as 'current standard' -- and nothing calls it. (2) That same document records a t_peak -> t_peak_net_load rename done 2026-08-23 because 'the ambiguous name directly caused a real analysis error mid-session'; the rename did not survive, the code carried t_peak again, and THE SAME CLASS OF ERROR RECURRED (four documents written stating the reserve constraint used gross demand when the hour selection has always been net-load based). STANDING CAUTION recorded in MODEL_WIDE_FINDINGS.md: documentation recording that something was fixed is not evidence that it is still fixed. DECISION NEEDED: whether to institute a periodic audit comparing documented fixes against code state, and if so at what cadence. RESOLVED 2026-09-12: scripts/audit_documented_fixes.py implements the check. CADENCE SET BY MODELER: hourly during an active session, and again whenever a session resumes after more than an hour idle. It greps and reads files; it does not solve. Five checks at present -- all_hours_reserve actually imported; t_peak stays renamed; and three superseded constants stay removed (GAS_CT_SPLIT_UNRESOLVED, GAS_CAPACITY_BASIS_UNRECONCILED, VA_HAY_ACRES_APPROX). It currently FAILS on all_hours_reserve BY DESIGN -- that is tracker #57 and the audit should keep failing until the module is wired in or the document is corrected. Protocol recorded in docs/README.md. | 1 | C
| 66 | [-> GitHub #8] No ramp constraints on any resource | lp_model.py contains no ramp-rate limits on gas or anything else -- two mentions of 'ramp', neither a constraint. Gas can go zero to full in one hour. ASSESSED 2026-09-12 as NOT needed for our own scenarios: the max 3-hour up-ramp in positive residual at 2045 is 22,131 MW against 86,906 MW of storage power, 3.9x headroom, and batteries have no meaningful ramp limit. CAISO's flexible ramping product exists because their ramp had to be met by gas turbines with real physical limits against undersized storage -- both absent here. BUT IT MATTERS FOR THE COMPARISON SCENARIOS: Scenario 1B (5% gas at 2045) and any Utility Preferred Plan lean on gas doing real work, and a CCGT realistically ramps 5-7%/minute from spinning with hours from cold. Unconstrained ramping FLATTERS the incumbent plan. That is the opposite of where the gap would be expected and is worth stating in the whitepaper. | 2 | NS
| 67 | [-> GitHub #9] CT-specific VOM constant missing | CCGT_VOM_MWH = 3.0 is applied to peakers. CT VOM is typically higher than CCGT (more starts, more cycling wear), so using the CCGT figure understates peaker marginal cost -- on top of the separate heat-rate question now resolved (fleet is frame at 11.0, not aeroderivative at 9.5). Both errors point the same way: peaker marginal cost is understated. Needed before the merit order is wired in, since ct_fleet is the rung most likely to be price-setting. | 3 | C
| 68 | [-> GitHub #10] Midday surplus — commercial demand flexibility | At 2045 the model has 3,722 surplus hours (42%), net load reaching -160 GW. That should drive midday prices to near zero and create a demand-side opportunity. Candidates identified 2026-09-12, strongest first: workplace EV charging (naturally midday-coincident with occupancy, no new hardware beyond managed charging); water and wastewater pumping (existing storage in elevated tanks and clearwells, deferrable within hours, aeration shiftable within dissolved-oxygen limits); heat pump water heating (tank as thermal battery; Dominion's Water Energy Rewards program already exists as a vehicle); refrigeration setpoint depression in grocery and cold storage; deferrable process loads. ICE STORAGE CAVEAT: conventional nocturnal charging is driven by CONDENSER EFFICIENCY at low ambient temperature, not merely off-peak pricing. Midday ice-making to absorb solar surplus trades cheap electricity against a worse COP on a hot afternoon -- a real engineering tradeoff, not a scheduling preference. BLOCKED BY ID 56: none of this can be valued while the dual is flat, since midday and evening look identical to the LP. Existing material in Appendix_DataCenter_DemandFlexibility_A7 (A.6 thermal storage, Water Energy Rewards) and Scenario3_Scope_and_Gaps (midday-surplus pricing treatment). | 2 | NS
| 69 | Dominion FRR/RPM status — capacity self-supply basis | ESTABLISHED 2026-09-11. Dominion is NOT currently an FRR entity. Timeline: RPM through 31 May 2021; elected FRR June 2021 or 2022 (two SCC documents disagree, unresolved); TERMINATED FRR 2 May 2024 per the SCC 2025 Combined Annual Report; the 2025 IRP confirms 'Dominion Energy currently participates in RPM capacity market'. APCo has always been FRR and is outside the DOM Zone. CONSEQUENCE: under RPM Dominion PROCURES its capacity obligation rather than self-supplying, so modelling Virginia as building its own capacity IS a conservative simplification. But smaller than it looks: PJM procured 134,205 MW of UCAP against a 134,414 MW requirement for 2026/27, and Dominion's own IRP calls the DOM Zone 'a net importer of energy'. Buying capacity requires someone else to have built it. OPEN: LS Power's FERC complaint arguing the FRR election should be invalidated, and the AG's stated intent to monitor SCC proceedings, mean further filings are likely. scc.virginia.gov disallows automated access; filings need manual download. Case numbers seen: PUR-2024-00193, PUR-2024-00184, PUR-2023-00066. | 3 | C
| 70 | [-> GitHub #11] IDX key rename — aliased now, full rename after first 2045 solve | A 2026-09-09 decision deliberately kept the short IDX keys ('g' through 'export') because driver.py and every solve_*.py script reference IDX['g'] directly, and renaming would cascade into files that change could not verify. THAT DECISION AGED THE WAY THE t_peak ONE DID: in review 'g' was described as 'the gas total' and the question came back -- total WHAT, fuel, cost, MWh? It is gas GENERATION in MW during hour t. 'gascum' is worse: it says cumulative gas without saying cumulative what, in what units, or what for. It is cumulative gas GENERATION in GWh, accumulating g * 0.001 hourly, existing only so the gas-share constraint can test a year-end total. 'Energy balance' is also vague -- the constraint is that supply equals demand in each hour. INTERIM 2026-09-12: SES_IDX_ALIASES plus _add_ses_aliases() give every short key an SES-compliant synonym addressing the same column, applied to all four IDX dicts. Legacy callers keep working; new code has no reason to use the short form. Aliases are only created for columns a given dict actually has (Rule 5) -- aliasing a non-existent column would be worse than no alias. FULL RENAME SCHEDULED for after the first successful 2045 solve, per modeler decision, so it can be verified against real solve data rather than assumed safe. Names agreed: gas_generation_mw, cumulative_gas_generation_gwh, hourly_supply_equals_demand (for the 'energy balance' constraint), equality_row_index / inequality_row_index (for 'row', which is NOT a running index but one variable reused and reset per block, eight times -- misusing it produced an A_eq of 175,566 rows against a b_eq of 61,325), and hourly_supply_demand_shadow_price_mwh for what scipy returns as res.eqlin.marginals. | 2 | IP
12 | 71 | Bath County capacity corrected to Dominion share | BATH_MW 3,000 -> 1,808 and BATH_MWH 24,000 -> 14,464. Dominion operates but owns 60%; 40% is Allegheny Generating Company and LS Power. Sourced to the 2024 Annual Report footnote (3) and 2025 IRP Figure 3.1.1.1. Reaches three problem builders and the reserve constraint. | High | C
13 | 72 | Gas retirement schedules A and B implemented | gas_baseline_mw(year, schedule) replaces a single Schedule B. Scenario 2 moved to Schedule A (physical retirement) -- Schedule B assumes plants close for lack of market, which is false where gas runs at a 68% capacity factor. Both schedules now share the 2041 and 2044 steps the old flat baseline omitted. | High | C
14 | 73 | Merit-order stack ported into Scenario 2 | build_scenario2_problem gains per-rung gas variables. Corrects fuel: effective heat rate 6.40 -> 8.12, $/MWh 44.32 -> 56.22. Also gives the hourly price variation storage needs, where a single rung leaves the energy-balance dual flat. | High | C
15 | 74 | C.2 distributed carve-out wired into Scenario 2 | Va. Code 56-585.5(C)(2) as raised by HB 628 / SB 175: 4.5%/5% of the RPS requirement from resources under 1 MW. Reaches 6,862 MW by 2045, 60% of new build. Clean share 34.7% -> 32.5%. | High | C
16 | 75 | Agrivoltaic siting applied as a cross-scenario overlay | 85% of solar installed after 2026, cost and land only. Previously carried by Scenario 3 alone, which gave that scenario a benefit stream the others were denied by construction. NREL sheep premium $0.07/W-DC; cattle refused for want of an equivalent figure. | Medium | C
17 | 76 | Brownfield screening curve method documented (Appendix Q) | Gas capacity sized by run-length against the CCGT minimum uptime, costed on the LEEMA four-term formulation. Measured 2045 gap: 10,263 MW of peaking duty, 1,233 blocks, median 2 hours. CT beats CCGT by $1,365M/yr. | High | C
18 | 77 | VirginiaOnlyLoad renamed VirginiaOnlyGeneration | The class returns the generation-side quantity while its name invited the meter-side reading; the two differ by the 9.25% loss factor. 45 occurrences across 19 files, no alias kept. | Medium | C
19 | 78 | Documentation structure: working documents, common reference, routing table | One working document per scenario indexed by topic; Common_Reference.md for cross-cutting facts; dashboard reduced to status only. Routing table names all four logs plus the citation register. | Medium | C
20 | 79 | New gas capacity costed into Scenario 2 annualised cost | The 2045 gap is measured and the technology settled, but the capex is not yet in the reported cost. | High | NS
21 | 80 | Gas price band across the compliance sweep | Deloitte MEDIUM and HIGH, EIA. Turns the cost curve into a band, which is what a cost-competitiveness claim requires. | Medium | NS

## Legend
Status Code | Meaning
NS | Not Started
DN | Decision Needed before work can proceed
Dx | Dependency — activity with ID x must be completed first (e.g., D1,2 means depends on both items 1 and 2)
C | Complete
IP | In process, currently working

## Graphical Views
View # | Description
1 | show modeler sanity check chart multi-day view by the request days as stacked barchart (combo stacked barchart and lines) with hourly generation in MWh as stacked bars as follows: nuclear on the bottom of the positive energy stack followed by battery discharge for each battery/storage type, then gas, then wind, then solar. Show hourly battery charging by battery/storage type in bars as a negative, and hourly curtailment (replaces export, which no longer exists in the corrected no-export model) as a negative bar alongside battery charging. Show hourly demand as a line. show hourly battery total SoC as a line with a separate scale 0-100% on the right.
2 | Show total storage SoC by week for the requested year
Loudoun-specific View #1 instances:
Built for 5 identified low-output windows (+/- 1 week each: Feb 2018, Sep 2018, Dec 2018, Nov/Dec 2015, Jan 2013) on the View1_* sheets. Adaptation note: nuclear, gas, and wind omitted (statewide/Dominion-zone assets, not modeled in this Loudoun-specific canopy/solar/battery analysis) -- curtailment IS included (excess solar the battery couldn't absorb), per the real spec. Battery: 1,551.2 MW / 100-hr duration / 80% RTE. Load derived as load_pct_of_peak x solar fleet MW (a stated placeholder scale, not Loudoun's real absolute load -- see Data_Sourcing_Log.md).

## View1_Feb2018
Timestamp | Solar (MW) | Battery Discharge (MW) | Battery Charging (MW, neg) | Curtailment (MW, neg) | Demand (MW) | SoC (%)
2018-02-16 09:00 | 66.33 | 1329.01 | 0 | 0 | 1395.34 | 99.14
2018-02-16 10:00 | 85.31 | 1310.03 | 0 | 0 | 1395.34 | 98.3
2018-02-16 11:00 | 92.39 | 1302.94 | 0 | 0 | 1395.34 | 97.46
2018-02-16 12:00 | 89.28 | 1306.05 | 0 | 0 | 1395.34 | 96.62
2018-02-16 13:00 | 68.15 | 1327.19 | 0 | 0 | 1395.34 | 95.76
2018-02-16 14:00 | 54.24 | 1341.09 | 0 | 0 | 1395.34 | 94.9
2018-02-16 15:00 | 34.17 | 1361.16 | 0 | 0 | 1395.34 | 94.02
2018-02-16 16:00 | 22.96 | 1372.38 | 0 | 0 | 1395.34 | 93.13
2018-02-16 17:00 | 6.4 | 1388.94 | 0 | 0 | 1395.34 | 92.24
2018-02-16 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 91.34
2018-02-16 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 90.44
2018-02-16 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 89.54
2018-02-16 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 88.64
2018-02-16 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 87.74
2018-02-16 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 86.84
2018-02-17 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 85.94
2018-02-17 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 85.04
2018-02-17 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 84.14
2018-02-17 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 83.24
2018-02-17 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 82.34
2018-02-17 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 81.44
2018-02-17 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 80.55
2018-02-17 07:00 | 46.04 | 1349.3 | 0 | 0 | 1395.34 | 79.68
2018-02-17 08:00 | 366.88 | 1028.46 | 0 | 0 | 1395.34 | 79.01
2018-02-17 09:00 | 691.59 | 703.75 | 0 | 0 | 1395.34 | 78.56
2018-02-17 10:00 | 898.79 | 496.55 | 0 | 0 | 1395.34 | 78.24
2018-02-17 11:00 | 247.77 | 1147.57 | 0 | 0 | 1395.34 | 77.5
2018-02-17 12:00 | 37.92 | 1357.41 | 0 | 0 | 1395.34 | 76.62
2018-02-17 13:00 | 34.93 | 1360.4 | 0 | 0 | 1395.34 | 75.75
2018-02-17 14:00 | 19.63 | 1375.7 | 0 | 0 | 1395.34 | 74.86
2018-02-17 15:00 | 26 | 1369.34 | 0 | 0 | 1395.34 | 73.98
2018-02-17 16:00 | 15.86 | 1379.48 | 0 | 0 | 1395.34 | 73.09
2018-02-17 17:00 | 6.1 | 1389.23 | 0 | 0 | 1395.34 | 72.19
2018-02-17 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 71.29
2018-02-17 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 70.39
2018-02-17 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 69.49
2018-02-17 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 68.59
2018-02-17 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 67.69
2018-02-17 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 66.8
2018-02-18 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 65.9
2018-02-18 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 65
2018-02-18 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 64.1
2018-02-18 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 63.2
2018-02-18 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 62.3
2018-02-18 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 61.4
2018-02-18 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 60.5
2018-02-18 07:00 | 24.63 | 1370.7 | 0 | 0 | 1395.34 | 59.61
2018-02-18 08:00 | 133.96 | 1261.38 | 0 | 0 | 1395.34 | 58.8
2018-02-18 09:00 | 223.37 | 1171.97 | 0 | 0 | 1395.34 | 58.05
2018-02-18 10:00 | 314.83 | 1080.51 | 0 | 0 | 1395.34 | 57.35
2018-02-18 11:00 | 715.04 | 680.3 | 0 | 0 | 1395.34 | 56.91
2018-02-18 12:00 | 866.26 | 529.08 | 0 | 0 | 1395.34 | 56.57
2018-02-18 13:00 | 953.19 | 442.15 | 0 | 0 | 1395.34 | 56.28
2018-02-18 14:00 | 944.13 | 451.2 | 0 | 0 | 1395.34 | 55.99
2018-02-18 15:00 | 746.42 | 648.92 | 0 | 0 | 1395.34 | 55.58
2018-02-18 16:00 | 379.45 | 1015.89 | 0 | 0 | 1395.34 | 54.92
2018-02-18 17:00 | 116.65 | 1278.69 | 0 | 0 | 1395.34 | 54.1
2018-02-18 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 53.2
2018-02-18 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 52.3
2018-02-18 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 51.4
2018-02-18 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 50.5
2018-02-18 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 49.6
2018-02-18 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 48.7
2018-02-19 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 47.8
2018-02-19 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 46.9
2018-02-19 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 46
2018-02-19 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 45.1
2018-02-19 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 44.2
2018-02-19 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 43.3
2018-02-19 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 42.4
2018-02-19 07:00 | 2.6 | 1392.74 | 0 | 0 | 1395.34 | 41.5
2018-02-19 08:00 | 118.62 | 1276.72 | 0 | 0 | 1395.34 | 40.68
2018-02-19 09:00 | 226.66 | 1168.68 | 0 | 0 | 1395.34 | 39.93
2018-02-19 10:00 | 119.7 | 1275.64 | 0 | 0 | 1395.34 | 39.11
2018-02-19 11:00 | 157.59 | 1237.75 | 0 | 0 | 1395.34 | 38.31
2018-02-19 12:00 | 101.23 | 1294.11 | 0 | 0 | 1395.34 | 37.47
2018-02-19 13:00 | 215.16 | 1180.17 | 0 | 0 | 1395.34 | 36.71
2018-02-19 14:00 | 206.72 | 1188.61 | 0 | 0 | 1395.34 | 35.95
2018-02-19 15:00 | 202.83 | 1192.51 | 0 | 0 | 1395.34 | 35.18
2018-02-19 16:00 | 172.49 | 1222.84 | 0 | 0 | 1395.34 | 34.39
2018-02-19 17:00 | 17.91 | 1377.43 | 0 | 0 | 1395.34 | 33.5
2018-02-19 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 32.6
2018-02-19 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 31.7
2018-02-19 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 30.8
2018-02-19 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 29.9
2018-02-19 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 29
2018-02-19 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 28.1
2018-02-20 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 27.21
2018-02-20 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 26.31
2018-02-20 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 25.41
2018-02-20 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 24.51
2018-02-20 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 23.61
2018-02-20 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 22.71
2018-02-20 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 21.81
2018-02-20 07:00 | 7 | 1388.34 | 0 | 0 | 1395.34 | 20.91
2018-02-20 08:00 | 122.1 | 1273.23 | 0 | 0 | 1395.34 | 20.09
2018-02-20 09:00 | 480.96 | 914.38 | 0 | 0 | 1395.34 | 19.5
2018-02-20 10:00 | 676.99 | 718.35 | 0 | 0 | 1395.34 | 19.04
2018-02-20 11:00 | 952.11 | 443.23 | 0 | 0 | 1395.34 | 18.75
2018-02-20 12:00 | 1032.68 | 362.66 | 0 | 0 | 1395.34 | 18.52
2018-02-20 13:00 | 1001.83 | 393.5 | 0 | 0 | 1395.34 | 18.27
2018-02-20 14:00 | 895.66 | 499.68 | 0 | 0 | 1395.34 | 17.94
2018-02-20 15:00 | 702.76 | 692.57 | 0 | 0 | 1395.34 | 17.5
2018-02-20 16:00 | 429.9 | 965.44 | 0 | 0 | 1395.34 | 16.88
2018-02-20 17:00 | 94.39 | 1300.95 | 0 | 0 | 1395.34 | 16.04
2018-02-20 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 15.14
2018-02-20 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 14.24
2018-02-20 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 13.34
2018-02-20 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 12.44
2018-02-20 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 11.54
2018-02-20 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 10.64
2018-02-21 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 9.74
2018-02-21 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 8.84
2018-02-21 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 7.94
2018-02-21 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 7.04
2018-02-21 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 6.14
2018-02-21 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 5.24
2018-02-21 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 4.34
2018-02-21 07:00 | 55.42 | 1339.91 | 0 | 0 | 1395.34 | 3.48
2018-02-21 08:00 | 235.33 | 1160 | 0 | 0 | 1395.34 | 2.73
2018-02-21 09:00 | 397.33 | 998 | 0 | 0 | 1395.34 | 2.09
2018-02-21 10:00 | 512.75 | 882.59 | 0 | 0 | 1395.34 | 1.52
2018-02-21 11:00 | 906.94 | 488.4 | 0 | 0 | 1395.34 | 1.2
2018-02-21 12:00 | 1006.24 | 389.1 | 0 | 0 | 1395.34 | 0.95
2018-02-21 13:00 | 845.58 | 549.76 | 0 | 0 | 1395.34 | 0.6
2018-02-21 14:00 | 364.91 | 929.06 | 0 | 0 | 1395.34 | 0
2018-02-21 15:00 | 497.7 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 16:00 | 401.19 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 17:00 | 101.56 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-21 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 07:00 | 6.93 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 08:00 | 63.89 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 09:00 | 31.54 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 10:00 | 31.59 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 11:00 | 67.34 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 12:00 | 48.06 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 13:00 | 136.48 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 14:00 | 38.62 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 15:00 | 19.57 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 16:00 | 15.05 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 17:00 | 5.84 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-22 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 07:00 | 23.23 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 08:00 | 156.26 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 09:00 | 62.79 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 10:00 | 52.01 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 11:00 | 79.72 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 12:00 | 71.27 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 13:00 | 151.42 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 14:00 | 120.81 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 15:00 | 128.42 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 16:00 | 95.18 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 17:00 | 9.6 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-23 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 07:00 | 2.8 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 08:00 | 34.62 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 09:00 | 45.11 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 10:00 | 57.07 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 11:00 | 59.41 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 12:00 | 64.76 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 13:00 | 49.72 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 14:00 | 54.83 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 15:00 | 39.45 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 16:00 | 62.47 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 17:00 | 23.18 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-24 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 08:00 | 25.92 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 09:00 | 54.28 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 10:00 | 45.28 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 11:00 | 19.43 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 12:00 | 38.82 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 13:00 | 58.35 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 14:00 | 101.25 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 15:00 | 76.59 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 16:00 | 56.29 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 17:00 | 23.19 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-25 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 07:00 | 11.04 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 08:00 | 30.04 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 09:00 | 77.2 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 10:00 | 130.53 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 11:00 | 138.19 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 12:00 | 242.99 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 13:00 | 272.44 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 14:00 | 227.35 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 15:00 | 163.24 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 16:00 | 81.52 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 17:00 | 58.37 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-26 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 07:00 | 83.37 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 08:00 | 412.19 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 09:00 | 702.83 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 10:00 | 886.64 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 11:00 | 1011.55 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 12:00 | 1078.76 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 13:00 | 1061.66 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 14:00 | 958.93 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 15:00 | 770.68 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 16:00 | 489.46 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 17:00 | 154.81 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-27 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 07:00 | 8.92 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 08:00 | 136.06 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 09:00 | 399.49 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 10:00 | 606.21 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 11:00 | 695.4 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 12:00 | 949.51 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 13:00 | 1035.82 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 14:00 | 673.81 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 15:00 | 324.92 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 16:00 | 129.72 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 17:00 | 56.33 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-02-28 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 07:00 | 5.81 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 08:00 | 31.9 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 09:00 | 25.2 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 10:00 | 65.12 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 11:00 | 112.9 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 12:00 | 202.7 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 13:00 | 137.62 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 14:00 | 96.9 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 15:00 | 48.27 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 16:00 | 21.06 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 17:00 | 6.16 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-01 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 07:00 | 15.98 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 08:00 | 136.73 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 09:00 | 301.78 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 10:00 | 334.61 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 11:00 | 249.55 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 12:00 | 365.32 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 13:00 | 469.79 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 14:00 | 650.56 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 15:00 | 762.78 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 16:00 | 527.12 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 17:00 | 128.73 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-02 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 07:00 | 104.16 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 08:00 | 456.03 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 09:00 | 780.63 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 10:00 | 1004.94 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 11:00 | 1141.77 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 12:00 | 1188.56 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 13:00 | 1149.35 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 14:00 | 1024.79 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 15:00 | 820.72 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 16:00 | 523.31 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 17:00 | 174.64 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 18:00 | 1.01 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-03 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 07:00 | 114.28 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 08:00 | 482.84 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 09:00 | 811.31 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 10:00 | 1036.05 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 11:00 | 1172.9 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 12:00 | 1212.8 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 13:00 | 1174.04 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 14:00 | 1044.5 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 15:00 | 836.13 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 16:00 | 544.56 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 17:00 | 185.47 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 18:00 | 1.55 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-04 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 07:00 | 124.32 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 08:00 | 497.28 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 09:00 | 816.83 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 10:00 | 1028.88 | 0 | 0 | 0 | 1395.34 | 0
2018-03-05 11:00 | 1163.78 | 0 | 0 | 0 | 1395.34 | 0
Summary
Total residual import (MWh): | 354989
Min SoC (%): | 0
Hours at 0% SoC: | 286
Max solar this window (MW): | 1212.8
Load this window (MW, flat): | 1395.3
Total curtailment this window (MWh): | 0

## View1_Sep2018
Timestamp | Solar (MW) | Battery Discharge (MW) | Battery Charging (MW, neg) | Curtailment (MW, neg) | Demand (MW) | SoC (%)
2018-09-01 11:00 | 328.07 | 1067.27 | 0 | 0 | 1395.34 | 99.31
2018-09-01 12:00 | 533.06 | 862.28 | 0 | 0 | 1395.34 | 98.76
2018-09-01 13:00 | 909.87 | 506.17 | 0 | 0 | 1416.04 | 98.43
2018-09-01 14:00 | 775.48 | 656.08 | 0 | 0 | 1431.56 | 98.01
2018-09-01 15:00 | 668.07 | 765.43 | 0 | 0 | 1433.5 | 97.51
2018-09-01 16:00 | 370.83 | 1040.34 | 0 | 0 | 1411.16 | 96.84
2018-09-01 17:00 | 125.05 | 1270.29 | 0 | 0 | 1395.34 | 96.02
2018-09-01 18:00 | 7.14 | 1388.19 | 0 | 0 | 1395.34 | 95.13
2018-09-01 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 94.23
2018-09-01 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 93.33
2018-09-01 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 92.43
2018-09-01 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 91.53
2018-09-01 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 90.63
2018-09-02 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 89.73
2018-09-02 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 88.83
2018-09-02 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 87.93
2018-09-02 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 87.03
2018-09-02 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 86.13
2018-09-02 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 85.23
2018-09-02 06:00 | 46.51 | 1348.83 | 0 | 0 | 1395.34 | 84.36
2018-09-02 07:00 | 252.52 | 1142.82 | 0 | 0 | 1395.34 | 83.63
2018-09-02 08:00 | 494.67 | 900.66 | 0 | 0 | 1395.34 | 83.05
2018-09-02 09:00 | 739.88 | 655.46 | 0 | 0 | 1395.34 | 82.62
2018-09-02 10:00 | 900.95 | 494.39 | 0 | 0 | 1395.34 | 82.31
2018-09-02 11:00 | 972.53 | 422.81 | 0 | 0 | 1395.34 | 82.03
2018-09-02 12:00 | 992.24 | 403.1 | 0 | 0 | 1395.34 | 81.77
2018-09-02 13:00 | 959.52 | 435.82 | 0 | 0 | 1395.34 | 81.49
2018-09-02 14:00 | 867.17 | 528.17 | 0 | 0 | 1395.34 | 81.15
2018-09-02 15:00 | 714.88 | 680.45 | 0 | 0 | 1395.34 | 80.71
2018-09-02 16:00 | 497.6 | 897.74 | 0 | 0 | 1395.34 | 80.13
2018-09-02 17:00 | 221.73 | 1173.61 | 0 | 0 | 1395.34 | 79.38
2018-09-02 18:00 | 24 | 1371.34 | 0 | 0 | 1395.34 | 78.49
2018-09-02 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 77.59
2018-09-02 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 76.7
2018-09-02 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 75.8
2018-09-02 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 74.9
2018-09-02 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 74
2018-09-03 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 73.1
2018-09-03 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 72.2
2018-09-03 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 71.3
2018-09-03 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 70.4
2018-09-03 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 69.5
2018-09-03 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 68.6
2018-09-03 06:00 | 45.78 | 1349.56 | 0 | 0 | 1395.34 | 67.73
2018-09-03 07:00 | 278.98 | 1116.36 | 0 | 0 | 1395.34 | 67.01
2018-09-03 08:00 | 547.56 | 847.77 | 0 | 0 | 1395.34 | 66.46
2018-09-03 09:00 | 744.03 | 651.3 | 0 | 0 | 1395.34 | 66.04
2018-09-03 10:00 | 872.89 | 522.45 | 0 | 0 | 1395.34 | 65.71
2018-09-03 11:00 | 963.65 | 431.69 | 0 | 0 | 1395.34 | 65.43
2018-09-03 12:00 | 994.67 | 400.67 | 0 | 0 | 1395.34 | 65.17
2018-09-03 13:00 | 875.13 | 520.21 | 0 | 0 | 1395.34 | 64.83
2018-09-03 14:00 | 793.84 | 601.5 | 0 | 0 | 1395.34 | 64.45
2018-09-03 15:00 | 659.29 | 736.05 | 0 | 0 | 1395.34 | 63.97
2018-09-03 16:00 | 392.94 | 1002.4 | 0 | 0 | 1395.34 | 63.33
2018-09-03 17:00 | 56.3 | 1339.03 | 0 | 0 | 1395.34 | 62.46
2018-09-03 18:00 | 19.07 | 1376.27 | 0 | 0 | 1395.34 | 61.58
2018-09-03 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 60.68
2018-09-03 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 59.78
2018-09-03 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 58.88
2018-09-03 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 57.98
2018-09-03 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 57.08
2018-09-04 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 56.18
2018-09-04 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 55.28
2018-09-04 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 54.38
2018-09-04 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 53.48
2018-09-04 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 52.58
2018-09-04 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 51.68
2018-09-04 06:00 | 43.82 | 1351.51 | 0 | 0 | 1395.34 | 50.81
2018-09-04 07:00 | 278.79 | 1116.55 | 0 | 0 | 1395.34 | 50.09
2018-09-04 08:00 | 554.23 | 841.11 | 0 | 0 | 1395.34 | 49.55
2018-09-04 09:00 | 762.05 | 633.29 | 0 | 0 | 1395.34 | 49.14
2018-09-04 10:00 | 906.56 | 488.77 | 0 | 0 | 1395.34 | 48.82
2018-09-04 11:00 | 978.67 | 416.67 | 0 | 0 | 1395.34 | 48.56
2018-09-04 12:00 | 993.94 | 401.4 | 0 | 0 | 1395.34 | 48.3
2018-09-04 13:00 | 872.35 | 522.99 | 0 | 0 | 1395.34 | 47.96
2018-09-04 14:00 | 461.65 | 933.69 | 0 | 0 | 1395.34 | 47.36
2018-09-04 15:00 | 368.92 | 1026.41 | 0 | 0 | 1395.34 | 46.7
2018-09-04 16:00 | 190.92 | 1204.42 | 0 | 0 | 1395.34 | 45.92
2018-09-04 17:00 | 121.33 | 1274.01 | 0 | 0 | 1395.34 | 45.1
2018-09-04 18:00 | 20.33 | 1375.01 | 0 | 0 | 1395.34 | 44.21
2018-09-04 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 43.31
2018-09-04 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 42.41
2018-09-04 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 41.51
2018-09-04 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 40.61
2018-09-04 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 39.71
2018-09-05 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 38.81
2018-09-05 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 37.92
2018-09-05 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 37.02
2018-09-05 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 36.12
2018-09-05 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 35.22
2018-09-05 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 34.32
2018-09-05 06:00 | 42.89 | 1352.45 | 0 | 0 | 1395.34 | 33.45
2018-09-05 07:00 | 271.73 | 1123.61 | 0 | 0 | 1395.34 | 32.72
2018-09-05 08:00 | 542.16 | 853.17 | 0 | 0 | 1395.34 | 32.17
2018-09-05 09:00 | 756.67 | 638.67 | 0 | 0 | 1395.34 | 31.76
2018-09-05 10:00 | 912.23 | 483.11 | 0 | 0 | 1395.34 | 31.45
2018-09-05 11:00 | 917.77 | 477.57 | 0 | 0 | 1395.34 | 31.14
2018-09-05 12:00 | 781.74 | 613.59 | 0 | 0 | 1395.34 | 30.74
2018-09-05 13:00 | 476.67 | 918.67 | 0 | 0 | 1395.34 | 30.15
2018-09-05 14:00 | 594.51 | 800.83 | 0 | 0 | 1395.34 | 29.64
2018-09-05 15:00 | 667.78 | 727.56 | 0 | 0 | 1395.34 | 29.17
2018-09-05 16:00 | 460.6 | 934.74 | 0 | 0 | 1395.34 | 28.56
2018-09-05 17:00 | 206.15 | 1189.19 | 0 | 0 | 1395.34 | 27.8
2018-09-05 18:00 | 18.73 | 1376.61 | 0 | 0 | 1395.34 | 26.91
2018-09-05 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 26.01
2018-09-05 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 25.11
2018-09-05 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 24.21
2018-09-05 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 23.31
2018-09-05 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 22.41
2018-09-06 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 21.51
2018-09-06 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 20.61
2018-09-06 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 19.71
2018-09-06 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 18.81
2018-09-06 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 17.91
2018-09-06 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 17.02
2018-09-06 06:00 | 41.95 | 1353.38 | 0 | 0 | 1395.34 | 16.14
2018-09-06 07:00 | 278.46 | 1116.87 | 0 | 0 | 1395.34 | 15.42
2018-09-06 08:00 | 555.33 | 840.01 | 0 | 0 | 1395.34 | 14.88
2018-09-06 09:00 | 765.98 | 629.36 | 0 | 0 | 1395.34 | 14.48
2018-09-06 10:00 | 902.3 | 493.04 | 0 | 0 | 1395.34 | 14.16
2018-09-06 11:00 | 979.48 | 415.86 | 0 | 0 | 1395.34 | 13.89
2018-09-06 12:00 | 988.94 | 406.4 | 0 | 0 | 1395.34 | 13.63
2018-09-06 13:00 | 693.82 | 701.52 | 0 | 0 | 1395.34 | 13.18
2018-09-06 14:00 | 784.02 | 615.25 | 0 | 0 | 1399.26 | 12.78
2018-09-06 15:00 | 568.53 | 831.1 | 0 | 0 | 1399.63 | 12.24
2018-09-06 16:00 | 326.67 | 1068.66 | 0 | 0 | 1395.34 | 11.55
2018-09-06 17:00 | 139.93 | 1255.41 | 0 | 0 | 1395.34 | 10.74
2018-09-06 18:00 | 14.04 | 1381.3 | 0 | 0 | 1395.34 | 9.85
2018-09-06 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 8.95
2018-09-06 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 8.06
2018-09-06 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 7.16
2018-09-06 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 6.26
2018-09-06 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 5.36
2018-09-07 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 4.46
2018-09-07 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 3.56
2018-09-07 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 2.66
2018-09-07 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 1.76
2018-09-07 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 0.86
2018-09-07 05:00 | 0 | 1332.88 | 0 | 0 | 1395.34 | 0
2018-09-07 06:00 | 32.17 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 07:00 | 229.98 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 08:00 | 451.42 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 09:00 | 628.13 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 10:00 | 892.56 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 11:00 | 806.54 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 12:00 | 736.26 | 0 | 0 | 0 | 1412.37 | 0
2018-09-07 13:00 | 579.79 | 0 | 0 | 0 | 1436.12 | 0
2018-09-07 14:00 | 570.2 | 0 | 0 | 0 | 1450.07 | 0
2018-09-07 15:00 | 441.04 | 0 | 0 | 0 | 1457.67 | 0
2018-09-07 16:00 | 333.7 | 0 | 0 | 0 | 1446.81 | 0
2018-09-07 17:00 | 99.84 | 0 | 0 | 0 | 1420.08 | 0
2018-09-07 18:00 | 8.84 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-07 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 06:00 | 10.88 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 07:00 | 35.87 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 08:00 | 140.76 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 09:00 | 178.05 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 10:00 | 172.16 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 11:00 | 111.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 12:00 | 94.66 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 13:00 | 76.57 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 14:00 | 109.03 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 15:00 | 80.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 16:00 | 32.32 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 17:00 | 36.13 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 18:00 | 1.41 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-08 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 06:00 | 2.12 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 07:00 | 6.91 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 08:00 | 27.54 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 09:00 | 59.46 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 10:00 | 89.5 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 11:00 | 101.61 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 12:00 | 83.62 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 13:00 | 102.85 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 14:00 | 83.37 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 15:00 | 73.2 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 16:00 | 23.04 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 17:00 | 30.06 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 18:00 | 0.27 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-09 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 06:00 | 15.17 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 07:00 | 55.47 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 08:00 | 29.8 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 09:00 | 53.32 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 10:00 | 57.79 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 11:00 | 103.03 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 12:00 | 87.96 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 13:00 | 97.07 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 14:00 | 96.17 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 15:00 | 84.73 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 16:00 | 46.37 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 17:00 | 102.2 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 18:00 | 9.77 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-10 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 06:00 | 27.67 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 07:00 | 41.34 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 08:00 | 36.84 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 09:00 | 84.75 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 10:00 | 171.3 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 11:00 | 203.54 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 12:00 | 200.91 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 13:00 | 233.33 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 14:00 | 176.13 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 15:00 | 172.6 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 16:00 | 60.21 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 17:00 | 38.03 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 18:00 | 1.41 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-11 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 06:00 | 2.49 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 07:00 | 38.91 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 08:00 | 98.95 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 09:00 | 113.45 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 10:00 | 152.84 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 11:00 | 264.32 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 12:00 | 552.12 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 13:00 | 426.67 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 14:00 | 613.34 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 15:00 | 682.2 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 16:00 | 342.99 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 17:00 | 171.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 18:00 | 5.52 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-12 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 06:00 | 34.89 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 07:00 | 213.65 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 08:00 | 336.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 09:00 | 323.57 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 10:00 | 240.01 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 11:00 | 146.81 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 12:00 | 297.83 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 13:00 | 348.75 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 14:00 | 268.81 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 15:00 | 319.06 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 16:00 | 400.88 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 17:00 | 167.27 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 18:00 | 5.31 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-13 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 06:00 | 33.92 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 07:00 | 86.64 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 08:00 | 74.16 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 09:00 | 118.05 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 10:00 | 95.13 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 11:00 | 232.62 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 12:00 | 208.94 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 13:00 | 148.11 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 14:00 | 268.15 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 15:00 | 170.44 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 16:00 | 196.37 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 17:00 | 94.5 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 18:00 | 2.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-14 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 06:00 | 7.87 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 07:00 | 40.05 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 08:00 | 100.02 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 09:00 | 198.14 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 10:00 | 460.5 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 11:00 | 435.78 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 12:00 | 556.64 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 13:00 | 517.37 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 14:00 | 480.18 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 15:00 | 331.66 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 16:00 | 246.82 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 17:00 | 90.57 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 18:00 | 2.92 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-15 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 06:00 | 33.16 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 07:00 | 225.81 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 08:00 | 118.42 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 09:00 | 195.17 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 10:00 | 325.33 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 11:00 | 616.61 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 12:00 | 777.53 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 13:00 | 838.42 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 14:00 | 519.83 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 15:00 | 620.2 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 16:00 | 425.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 17:00 | 138.36 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 18:00 | 2.8 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-16 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 06:00 | 4.45 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 07:00 | 20.3 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 08:00 | 47.99 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 09:00 | 111.76 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 10:00 | 201.37 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 11:00 | 90.87 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 12:00 | 71.33 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 13:00 | 112.06 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 14:00 | 95.36 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 15:00 | 193.98 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 16:00 | 107.59 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 17:00 | 131.07 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-17 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 06:00 | 9.08 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 07:00 | 95.96 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 08:00 | 140.09 | 0 | 0 | 0 | 1395.34 | 0
2018-09-18 09:00 | 247.75 | 0 | 0 | 0 | 1395.34 | 0
Summary
Total residual import (MWh): | 346118
Min SoC (%): | 0
Hours at 0% SoC: | 269
Max solar this window (MW): | 994.7
Load this window (MW, flat): | 1457.7
Total curtailment this window (MWh): | 0

## View1_Dec2018
Timestamp | Solar (MW) | Battery Discharge (MW) | Battery Charging (MW, neg) | Curtailment (MW, neg) | Demand (MW) | SoC (%)
2018-12-06 16:00 | 25.72 | 1369.62 | 0 | 0 | 1395.34 | 99.12
2018-12-06 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 98.22
2018-12-06 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 97.32
2018-12-06 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 96.42
2018-12-06 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 95.52
2018-12-06 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 94.62
2018-12-06 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 93.72
2018-12-06 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 92.82
2018-12-07 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 91.92
2018-12-07 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 91.02
2018-12-07 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 90.12
2018-12-07 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 89.22
2018-12-07 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 88.32
2018-12-07 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 87.42
2018-12-07 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 86.52
2018-12-07 07:00 | 15.92 | 1379.42 | 0 | 0 | 1395.34 | 85.63
2018-12-07 08:00 | 298.91 | 1096.43 | 0 | 0 | 1395.34 | 84.93
2018-12-07 09:00 | 608.54 | 786.8 | 0 | 0 | 1395.34 | 84.42
2018-12-07 10:00 | 813.49 | 581.85 | 0 | 0 | 1395.34 | 84.05
2018-12-07 11:00 | 924.17 | 471.16 | 0 | 0 | 1395.34 | 83.74
2018-12-07 12:00 | 946.33 | 449.01 | 0 | 0 | 1395.34 | 83.45
2018-12-07 13:00 | 877.19 | 518.14 | 0 | 0 | 1395.34 | 83.12
2018-12-07 14:00 | 721.68 | 673.66 | 0 | 0 | 1395.34 | 82.68
2018-12-07 15:00 | 460.58 | 934.76 | 0 | 0 | 1395.34 | 82.08
2018-12-07 16:00 | 124.17 | 1271.17 | 0 | 0 | 1395.34 | 81.26
2018-12-07 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 80.36
2018-12-07 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 79.46
2018-12-07 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 78.56
2018-12-07 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 77.66
2018-12-07 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 76.76
2018-12-07 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 75.86
2018-12-07 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 74.97
2018-12-08 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 74.07
2018-12-08 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 73.17
2018-12-08 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 72.27
2018-12-08 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 71.37
2018-12-08 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 70.47
2018-12-08 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 69.57
2018-12-08 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 68.67
2018-12-08 07:00 | 1.45 | 1393.88 | 0 | 0 | 1395.34 | 67.77
2018-12-08 08:00 | 111.29 | 1284.04 | 0 | 0 | 1395.34 | 66.94
2018-12-08 09:00 | 250.6 | 1144.74 | 0 | 0 | 1395.34 | 66.2
2018-12-08 10:00 | 309.25 | 1086.08 | 0 | 0 | 1395.34 | 65.5
2018-12-08 11:00 | 559.44 | 835.89 | 0 | 0 | 1395.34 | 64.97
2018-12-08 12:00 | 892.39 | 502.95 | 0 | 0 | 1395.34 | 64.64
2018-12-08 13:00 | 615.16 | 780.18 | 0 | 0 | 1395.34 | 64.14
2018-12-08 14:00 | 452.44 | 942.9 | 0 | 0 | 1395.34 | 63.53
2018-12-08 15:00 | 226.53 | 1168.81 | 0 | 0 | 1395.34 | 62.78
2018-12-08 16:00 | 38.83 | 1356.5 | 0 | 0 | 1395.34 | 61.9
2018-12-08 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 61
2018-12-08 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 60.1
2018-12-08 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 59.2
2018-12-08 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 58.3
2018-12-08 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 57.4
2018-12-08 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 56.5
2018-12-08 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 55.61
2018-12-09 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 54.71
2018-12-09 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 53.81
2018-12-09 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 52.91
2018-12-09 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 52.01
2018-12-09 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 51.11
2018-12-09 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 50.21
2018-12-09 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 49.31
2018-12-09 07:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 48.41
2018-12-09 08:00 | 29.98 | 1365.36 | 0 | 0 | 1395.34 | 47.53
2018-12-09 09:00 | 50.23 | 1345.1 | 0 | 0 | 1395.34 | 46.66
2018-12-09 10:00 | 54.4 | 1340.93 | 0 | 0 | 1395.34 | 45.8
2018-12-09 11:00 | 82.69 | 1312.65 | 0 | 0 | 1395.34 | 44.95
2018-12-09 12:00 | 88.45 | 1306.89 | 0 | 0 | 1395.34 | 44.11
2018-12-09 13:00 | 42.75 | 1352.59 | 0 | 0 | 1395.34 | 43.24
2018-12-09 14:00 | 32.01 | 1363.33 | 0 | 0 | 1395.34 | 42.36
2018-12-09 15:00 | 19.75 | 1375.59 | 0 | 0 | 1395.34 | 41.47
2018-12-09 16:00 | 4.82 | 1390.52 | 0 | 0 | 1395.34 | 40.57
2018-12-09 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 39.68
2018-12-09 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 38.78
2018-12-09 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 37.88
2018-12-09 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 36.98
2018-12-09 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 36.08
2018-12-09 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 35.18
2018-12-09 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 34.28
2018-12-10 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 33.38
2018-12-10 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 32.48
2018-12-10 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 31.58
2018-12-10 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 30.68
2018-12-10 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 29.78
2018-12-10 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 28.88
2018-12-10 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 27.98
2018-12-10 07:00 | 0.29 | 1395.05 | 0 | 0 | 1395.34 | 27.08
2018-12-10 08:00 | 127.9 | 1267.43 | 0 | 0 | 1395.34 | 26.27
2018-12-10 09:00 | 356.5 | 1038.83 | 0 | 0 | 1395.34 | 25.6
2018-12-10 10:00 | 552.11 | 843.23 | 0 | 0 | 1395.34 | 25.05
2018-12-10 11:00 | 569.78 | 825.56 | 0 | 0 | 1395.34 | 24.52
2018-12-10 12:00 | 609.23 | 786.11 | 0 | 0 | 1395.34 | 24.01
2018-12-10 13:00 | 642.93 | 752.41 | 0 | 0 | 1395.34 | 23.53
2018-12-10 14:00 | 605.39 | 789.94 | 0 | 0 | 1395.34 | 23.02
2018-12-10 15:00 | 426.87 | 968.46 | 0 | 0 | 1395.34 | 22.39
2018-12-10 16:00 | 120.88 | 1274.45 | 0 | 0 | 1395.34 | 21.57
2018-12-10 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 20.67
2018-12-10 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 19.77
2018-12-10 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 18.87
2018-12-10 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 17.97
2018-12-10 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 17.07
2018-12-10 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 16.18
2018-12-10 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 15.28
2018-12-11 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 14.38
2018-12-11 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 13.48
2018-12-11 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 12.58
2018-12-11 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 11.68
2018-12-11 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 10.78
2018-12-11 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 9.88
2018-12-11 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 8.98
2018-12-11 07:00 | 10.7 | 1384.64 | 0 | 0 | 1395.34 | 8.09
2018-12-11 08:00 | 277.37 | 1117.97 | 0 | 0 | 1395.34 | 7.37
2018-12-11 09:00 | 599.18 | 796.16 | 0 | 0 | 1395.34 | 6.85
2018-12-11 10:00 | 808.99 | 586.35 | 0 | 0 | 1395.34 | 6.47
2018-12-11 11:00 | 913.42 | 481.92 | 0 | 0 | 1395.34 | 6.16
2018-12-11 12:00 | 927.89 | 467.44 | 0 | 0 | 1395.34 | 5.86
2018-12-11 13:00 | 852.14 | 543.2 | 0 | 0 | 1395.34 | 5.51
2018-12-11 14:00 | 702.08 | 693.26 | 0 | 0 | 1395.34 | 5.07
2018-12-11 15:00 | 456.02 | 939.31 | 0 | 0 | 1395.34 | 4.46
2018-12-11 16:00 | 123.78 | 1271.55 | 0 | 0 | 1395.34 | 3.64
2018-12-11 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 2.74
2018-12-11 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 1.84
2018-12-11 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 0.94
2018-12-11 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 0.04
2018-12-11 21:00 | 0 | 65.51 | 0 | 0 | 1395.34 | 0
2018-12-11 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-11 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 07:00 | 7.76 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 08:00 | 244.91 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 09:00 | 412.69 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 10:00 | 640.54 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 11:00 | 815.16 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 12:00 | 454.74 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 13:00 | 417.31 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 14:00 | 160.41 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 15:00 | 116.58 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 16:00 | 25.38 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-12 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 07:00 | 4.49 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 08:00 | 209.56 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 09:00 | 499.68 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 10:00 | 708.58 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 11:00 | 672.37 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 12:00 | 615.38 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 13:00 | 777.51 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 14:00 | 507.49 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 15:00 | 280.85 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 16:00 | 29.06 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-13 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 08:00 | 44.6 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 09:00 | 87.64 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 10:00 | 105.31 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 11:00 | 76.72 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 12:00 | 29.7 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 13:00 | 36.68 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 14:00 | 39.45 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 15:00 | 18.05 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 16:00 | 2.93 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-14 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 08:00 | 1.27 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 09:00 | 0.3 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 10:00 | 20.74 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 11:00 | 52.96 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 12:00 | 61.33 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 13:00 | 77.88 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 14:00 | 63.36 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 15:00 | 16.88 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 16:00 | 2.21 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-15 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 08:00 | 21.45 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 09:00 | 6.37 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 10:00 | 30.23 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 11:00 | 90.44 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 12:00 | 126 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 13:00 | 52.25 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 14:00 | 48.59 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 15:00 | 225.63 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 16:00 | 102.1 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-16 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 07:00 | 5.12 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 08:00 | 205.67 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 09:00 | 290.54 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 10:00 | 279.6 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 11:00 | 723.66 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 12:00 | 676.51 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 13:00 | 709.94 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 14:00 | 501.44 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 15:00 | 310.46 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 16:00 | 128.72 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-17 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 07:00 | 5.92 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 08:00 | 247.27 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 09:00 | 568.65 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 10:00 | 787.45 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 11:00 | 902.1 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 12:00 | 929.07 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 13:00 | 867.73 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 14:00 | 714.14 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 15:00 | 466.97 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 16:00 | 139.52 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-18 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 07:00 | 4.25 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 08:00 | 210.73 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 09:00 | 413.56 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 10:00 | 416.01 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 11:00 | 532.95 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 12:00 | 619.23 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 13:00 | 734.2 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 14:00 | 675.47 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 15:00 | 426.37 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 16:00 | 109.11 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-19 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 08:00 | 14.09 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 09:00 | 21.88 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 10:00 | 23.98 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 11:00 | 54.66 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 12:00 | 58.39 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 13:00 | 26.75 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 14:00 | 13.16 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 15:00 | 2.76 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 16:00 | 0.06 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-20 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 08:00 | 81.34 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 09:00 | 294.9 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 10:00 | 491.59 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 11:00 | 441.54 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 12:00 | 778.03 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 13:00 | 666.99 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 14:00 | 474.82 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 15:00 | 305.1 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 16:00 | 81.75 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-21 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 07:00 | 0.82 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 08:00 | 105.16 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 09:00 | 367.11 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 10:00 | 655.06 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 11:00 | 646.72 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 12:00 | 432.74 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 13:00 | 800.05 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 14:00 | 677.39 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 15:00 | 409.79 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 16:00 | 106.27 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-22 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 07:00 | 2.79 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 08:00 | 204.68 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 09:00 | 503.94 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 10:00 | 719.21 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 11:00 | 837.49 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 12:00 | 803.79 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 13:00 | 264.57 | 0 | 0 | 0 | 1395.34 | 0
2018-12-23 14:00 | 70.32 | 0 | 0 | 0 | 1395.34 | 0
Summary
Total residual import (MWh): | 359336
Min SoC (%): | 0
Hours at 0% SoC: | 282
Max solar this window (MW): | 946.3
Load this window (MW, flat): | 1395.3
Total curtailment this window (MWh): | 0

## View1_NovDec2015
Timestamp | Solar (MW) | Battery Discharge (MW) | Battery Charging (MW, neg) | Curtailment (MW, neg) | Demand (MW) | SoC (%)
2015-11-21 14:00 | 711.66 | 683.67 | 0 | 0 | 1395.34 | 99.56
2015-11-21 15:00 | 459.28 | 936.06 | 0 | 0 | 1395.34 | 98.96
2015-11-21 16:00 | 132.66 | 1262.68 | 0 | 0 | 1395.34 | 98.14
2015-11-21 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 97.24
2015-11-21 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 96.34
2015-11-21 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 95.44
2015-11-21 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 94.54
2015-11-21 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 93.64
2015-11-21 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 92.74
2015-11-21 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 91.85
2015-11-22 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 90.95
2015-11-22 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 90.05
2015-11-22 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 89.15
2015-11-22 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 88.25
2015-11-22 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 87.35
2015-11-22 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 86.45
2015-11-22 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 85.55
2015-11-22 07:00 | 16.15 | 1379.19 | 0 | 0 | 1395.34 | 84.66
2015-11-22 08:00 | 212.8 | 1182.54 | 0 | 0 | 1395.34 | 83.9
2015-11-22 09:00 | 357.7 | 1037.64 | 0 | 0 | 1395.34 | 83.23
2015-11-22 10:00 | 629.76 | 765.57 | 0 | 0 | 1395.34 | 82.73
2015-11-22 11:00 | 728 | 667.34 | 0 | 0 | 1395.34 | 82.3
2015-11-22 12:00 | 464.69 | 930.65 | 0 | 0 | 1395.34 | 81.7
2015-11-22 13:00 | 379.3 | 1016.04 | 0 | 0 | 1395.34 | 81.05
2015-11-22 14:00 | 312.95 | 1082.39 | 0 | 0 | 1395.34 | 80.35
2015-11-22 15:00 | 261.98 | 1133.36 | 0 | 0 | 1395.34 | 79.62
2015-11-22 16:00 | 31.66 | 1363.68 | 0 | 0 | 1395.34 | 78.74
2015-11-22 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 77.84
2015-11-22 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 76.94
2015-11-22 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 76.04
2015-11-22 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 75.14
2015-11-22 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 74.24
2015-11-22 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 73.34
2015-11-22 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 72.45
2015-11-23 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 71.55
2015-11-23 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 70.65
2015-11-23 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 69.75
2015-11-23 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 68.85
2015-11-23 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 67.95
2015-11-23 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 67.05
2015-11-23 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 66.15
2015-11-23 07:00 | 44.43 | 1350.91 | 0 | 0 | 1395.34 | 65.28
2015-11-23 08:00 | 372.95 | 1022.39 | 0 | 0 | 1395.34 | 64.62
2015-11-23 09:00 | 679.47 | 715.86 | 0 | 0 | 1395.34 | 64.16
2015-11-23 10:00 | 874.63 | 520.7 | 0 | 0 | 1395.34 | 63.82
2015-11-23 11:00 | 973.99 | 421.35 | 0 | 0 | 1395.34 | 63.55
2015-11-23 12:00 | 982.57 | 412.76 | 0 | 0 | 1395.34 | 63.28
2015-11-23 13:00 | 908.78 | 486.56 | 0 | 0 | 1395.34 | 62.97
2015-11-23 14:00 | 745.07 | 650.27 | 0 | 0 | 1395.34 | 62.55
2015-11-23 15:00 | 477.03 | 918.3 | 0 | 0 | 1395.34 | 61.96
2015-11-23 16:00 | 137.82 | 1257.52 | 0 | 0 | 1395.34 | 61.15
2015-11-23 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 60.25
2015-11-23 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 59.35
2015-11-23 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 58.45
2015-11-23 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 57.55
2015-11-23 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 56.65
2015-11-23 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 55.75
2015-11-23 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 54.85
2015-11-24 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 53.95
2015-11-24 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 53.05
2015-11-24 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 52.15
2015-11-24 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 51.25
2015-11-24 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 50.35
2015-11-24 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 49.45
2015-11-24 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 48.55
2015-11-24 07:00 | 35.46 | 1359.88 | 0 | 0 | 1395.34 | 47.68
2015-11-24 08:00 | 256.69 | 1138.65 | 0 | 0 | 1395.34 | 46.94
2015-11-24 09:00 | 627.5 | 767.83 | 0 | 0 | 1395.34 | 46.45
2015-11-24 10:00 | 815.35 | 579.99 | 0 | 0 | 1395.34 | 46.08
2015-11-24 11:00 | 466.33 | 929 | 0 | 0 | 1395.34 | 45.48
2015-11-24 12:00 | 924.85 | 470.49 | 0 | 0 | 1395.34 | 45.17
2015-11-24 13:00 | 738.57 | 656.77 | 0 | 0 | 1395.34 | 44.75
2015-11-24 14:00 | 695.29 | 700.05 | 0 | 0 | 1395.34 | 44.3
2015-11-24 15:00 | 441.53 | 953.8 | 0 | 0 | 1395.34 | 43.68
2015-11-24 16:00 | 125.58 | 1269.75 | 0 | 0 | 1395.34 | 42.87
2015-11-24 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 41.97
2015-11-24 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 41.07
2015-11-24 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 40.17
2015-11-24 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 39.27
2015-11-24 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 38.37
2015-11-24 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 37.47
2015-11-24 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 36.57
2015-11-25 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 35.67
2015-11-25 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 34.77
2015-11-25 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 33.87
2015-11-25 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 32.97
2015-11-25 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 32.07
2015-11-25 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 31.17
2015-11-25 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 30.27
2015-11-25 07:00 | 28.55 | 1366.78 | 0 | 0 | 1395.34 | 29.39
2015-11-25 08:00 | 317.32 | 1078.01 | 0 | 0 | 1395.34 | 28.7
2015-11-25 09:00 | 602.17 | 793.17 | 0 | 0 | 1395.34 | 28.18
2015-11-25 10:00 | 797.62 | 597.71 | 0 | 0 | 1395.34 | 27.8
2015-11-25 11:00 | 886.24 | 509.1 | 0 | 0 | 1395.34 | 27.47
2015-11-25 12:00 | 897.54 | 497.8 | 0 | 0 | 1395.34 | 27.15
2015-11-25 13:00 | 828.84 | 566.5 | 0 | 0 | 1395.34 | 26.78
2015-11-25 14:00 | 679 | 716.34 | 0 | 0 | 1395.34 | 26.32
2015-11-25 15:00 | 431.3 | 964.04 | 0 | 0 | 1395.34 | 25.7
2015-11-25 16:00 | 121.15 | 1274.19 | 0 | 0 | 1395.34 | 24.88
2015-11-25 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 23.98
2015-11-25 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 23.08
2015-11-25 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 22.18
2015-11-25 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 21.28
2015-11-25 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 20.38
2015-11-25 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 19.48
2015-11-25 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 18.58
2015-11-26 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 17.68
2015-11-26 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 16.78
2015-11-26 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 15.88
2015-11-26 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 14.99
2015-11-26 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 14.09
2015-11-26 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 13.19
2015-11-26 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 12.29
2015-11-26 07:00 | 25.68 | 1369.66 | 0 | 0 | 1395.34 | 11.4
2015-11-26 08:00 | 304.05 | 1091.29 | 0 | 0 | 1395.34 | 10.7
2015-11-26 09:00 | 580.89 | 814.44 | 0 | 0 | 1395.34 | 10.18
2015-11-26 10:00 | 773.18 | 622.16 | 0 | 0 | 1395.34 | 9.77
2015-11-26 11:00 | 866.14 | 529.19 | 0 | 0 | 1395.34 | 9.43
2015-11-26 12:00 | 641.15 | 754.19 | 0 | 0 | 1395.34 | 8.95
2015-11-26 13:00 | 812.78 | 582.56 | 0 | 0 | 1395.34 | 8.57
2015-11-26 14:00 | 662.12 | 733.22 | 0 | 0 | 1395.34 | 8.1
2015-11-26 15:00 | 419.12 | 976.21 | 0 | 0 | 1395.34 | 7.47
2015-11-26 16:00 | 103.33 | 1292.01 | 0 | 0 | 1395.34 | 6.64
2015-11-26 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 5.74
2015-11-26 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 4.84
2015-11-26 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 3.94
2015-11-26 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 3.04
2015-11-26 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 2.14
2015-11-26 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 1.24
2015-11-26 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 0.34
2015-11-27 00:00 | 0 | 526.86 | 0 | 0 | 1395.34 | 0
2015-11-27 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 07:00 | 6.86 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 08:00 | 143.67 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 09:00 | 414.26 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 10:00 | 631.73 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 11:00 | 788.86 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 12:00 | 587.1 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 13:00 | 608.09 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 14:00 | 502.93 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 15:00 | 422.56 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 16:00 | 117.86 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-27 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 07:00 | 2.24 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 08:00 | 62.5 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 09:00 | 183.64 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 10:00 | 472.31 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 11:00 | 482.3 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 12:00 | 355.44 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 13:00 | 184.6 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 14:00 | 124.41 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 15:00 | 49.71 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 16:00 | 22.7 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-28 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 08:00 | 23.06 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 09:00 | 82.05 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 10:00 | 100.54 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 11:00 | 93.26 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 12:00 | 83.55 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 13:00 | 80.38 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 14:00 | 8.53 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 15:00 | 63.97 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 16:00 | 7.48 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-29 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 07:00 | 2.03 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 08:00 | 32.9 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 09:00 | 114.33 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 10:00 | 98.35 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 11:00 | 127.57 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 12:00 | 152.61 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 13:00 | 143.33 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 14:00 | 67.6 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 15:00 | 84.03 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 16:00 | 18.47 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-11-30 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 08:00 | 21.27 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 09:00 | 42.86 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 10:00 | 84.51 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 11:00 | 169.14 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 12:00 | 121.82 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 13:00 | 154.43 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 14:00 | 158.58 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 15:00 | 76.96 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 16:00 | 19.73 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-01 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 08:00 | 29.75 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 09:00 | 92.01 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 10:00 | 48.77 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 11:00 | 46.6 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 12:00 | 119.31 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 13:00 | 91.52 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 14:00 | 43.4 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 15:00 | 81.05 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 16:00 | 11.28 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-02 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 07:00 | 21.38 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 08:00 | 300.72 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 09:00 | 604.87 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 10:00 | 813.46 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 11:00 | 659.99 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 12:00 | 783.77 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 13:00 | 863.08 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 14:00 | 393.62 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 15:00 | 317.12 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 16:00 | 115.82 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-03 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 07:00 | 19.79 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 08:00 | 303 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 09:00 | 607.68 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 10:00 | 809.7 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 11:00 | 910.45 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 12:00 | 925.93 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 13:00 | 850.75 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 14:00 | 700.92 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 15:00 | 450.44 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 16:00 | 125.35 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-04 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 07:00 | 16.85 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 08:00 | 289.77 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 09:00 | 587.93 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 10:00 | 775.77 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 11:00 | 870.87 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 12:00 | 887.23 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 13:00 | 823.49 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 14:00 | 679.21 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 15:00 | 439.58 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 16:00 | 121.79 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-05 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 07:00 | 15.57 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 08:00 | 278.84 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 09:00 | 575.29 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 10:00 | 772.9 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 11:00 | 876.3 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 12:00 | 753.51 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 13:00 | 718.21 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 14:00 | 480.63 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 15:00 | 165.19 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 16:00 | 47.96 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-06 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 07:00 | 14.73 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 08:00 | 272.94 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 09:00 | 568.3 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 10:00 | 754.53 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 11:00 | 843.04 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 12:00 | 846.46 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 13:00 | 783.43 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 14:00 | 646.25 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 15:00 | 293.39 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 16:00 | 65.92 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-07 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 07:00 | 12.75 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 08:00 | 266.25 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 09:00 | 561.66 | 0 | 0 | 0 | 1395.34 | 0
2015-12-08 10:00 | 748.04 | 0 | 0 | 0 | 1395.34 | 0
Summary
Total residual import (MWh): | 346798
Min SoC (%): | 0
Hours at 0% SoC: | 275
Max solar this window (MW): | 982.6
Load this window (MW, flat): | 1395.3
Total curtailment this window (MWh): | 0

## View1_Jan2013
Timestamp | Solar (MW) | Battery Discharge (MW) | Battery Charging (MW, neg) | Curtailment (MW, neg) | Demand (MW) | SoC (%)
2013-01-07 13:00 | 692.77 | 702.57 | 0 | 0 | 1395.34 | 99.55
2013-01-07 14:00 | 734.13 | 661.2 | 0 | 0 | 1395.34 | 99.12
2013-01-07 15:00 | 510.15 | 885.19 | 0 | 0 | 1395.34 | 98.55
2013-01-07 16:00 | 203.93 | 1191.41 | 0 | 0 | 1395.34 | 97.78
2013-01-07 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 96.88
2013-01-07 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 95.98
2013-01-07 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 95.08
2013-01-07 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 94.18
2013-01-07 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 93.28
2013-01-07 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 92.39
2013-01-07 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 91.49
2013-01-08 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 90.59
2013-01-08 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 89.69
2013-01-08 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 88.79
2013-01-08 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 87.89
2013-01-08 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 86.99
2013-01-08 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 86.09
2013-01-08 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 85.19
2013-01-08 07:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 84.29
2013-01-08 08:00 | 197.94 | 1197.4 | 0 | 0 | 1395.34 | 83.52
2013-01-08 09:00 | 528.76 | 866.58 | 0 | 0 | 1395.34 | 82.96
2013-01-08 10:00 | 464.37 | 930.97 | 0 | 0 | 1395.34 | 82.36
2013-01-08 11:00 | 642.96 | 752.38 | 0 | 0 | 1395.34 | 81.87
2013-01-08 12:00 | 748.34 | 646.99 | 0 | 0 | 1395.34 | 81.46
2013-01-08 13:00 | 604.5 | 790.84 | 0 | 0 | 1395.34 | 80.95
2013-01-08 14:00 | 735.3 | 660.04 | 0 | 0 | 1395.34 | 80.52
2013-01-08 15:00 | 511.7 | 883.63 | 0 | 0 | 1395.34 | 79.95
2013-01-08 16:00 | 208.04 | 1187.3 | 0 | 0 | 1395.34 | 79.19
2013-01-08 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 78.29
2013-01-08 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 77.39
2013-01-08 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 76.49
2013-01-08 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 75.59
2013-01-08 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 74.69
2013-01-08 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 73.79
2013-01-08 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 72.89
2013-01-09 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 71.99
2013-01-09 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 71.09
2013-01-09 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 70.19
2013-01-09 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 69.29
2013-01-09 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 68.39
2013-01-09 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 67.49
2013-01-09 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 66.59
2013-01-09 07:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 65.69
2013-01-09 08:00 | 75.02 | 1320.32 | 0 | 0 | 1395.34 | 64.84
2013-01-09 09:00 | 212.11 | 1183.23 | 0 | 0 | 1395.34 | 64.08
2013-01-09 10:00 | 412.25 | 983.09 | 0 | 0 | 1395.34 | 63.45
2013-01-09 11:00 | 343.06 | 1052.27 | 0 | 0 | 1395.34 | 62.77
2013-01-09 12:00 | 300.28 | 1095.05 | 0 | 0 | 1395.34 | 62.06
2013-01-09 13:00 | 177.93 | 1217.41 | 0 | 0 | 1395.34 | 61.28
2013-01-09 14:00 | 28.11 | 1367.23 | 0 | 0 | 1395.34 | 60.4
2013-01-09 15:00 | 18.84 | 1376.49 | 0 | 0 | 1395.34 | 59.51
2013-01-09 16:00 | 10.78 | 1384.56 | 0 | 0 | 1395.34 | 58.62
2013-01-09 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 57.72
2013-01-09 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 56.82
2013-01-09 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 55.92
2013-01-09 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 55.02
2013-01-09 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 54.12
2013-01-09 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 53.22
2013-01-09 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 52.32
2013-01-10 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 51.42
2013-01-10 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 50.52
2013-01-10 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 49.62
2013-01-10 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 48.72
2013-01-10 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 47.82
2013-01-10 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 46.92
2013-01-10 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 46.02
2013-01-10 07:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 45.12
2013-01-10 08:00 | 78.99 | 1316.35 | 0 | 0 | 1395.34 | 44.27
2013-01-10 09:00 | 397.66 | 997.68 | 0 | 0 | 1395.34 | 43.63
2013-01-10 10:00 | 759.54 | 635.8 | 0 | 0 | 1395.34 | 43.22
2013-01-10 11:00 | 881.11 | 514.23 | 0 | 0 | 1395.34 | 42.89
2013-01-10 12:00 | 917.1 | 478.24 | 0 | 0 | 1395.34 | 42.58
2013-01-10 13:00 | 865.71 | 529.63 | 0 | 0 | 1395.34 | 42.24
2013-01-10 14:00 | 743.94 | 651.39 | 0 | 0 | 1395.34 | 41.82
2013-01-10 15:00 | 533.46 | 861.88 | 0 | 0 | 1395.34 | 41.26
2013-01-10 16:00 | 53.99 | 1341.34 | 0 | 0 | 1395.34 | 40.4
2013-01-10 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 39.5
2013-01-10 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 38.6
2013-01-10 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 37.7
2013-01-10 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 36.8
2013-01-10 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 35.9
2013-01-10 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 35
2013-01-10 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 34.1
2013-01-11 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 33.2
2013-01-11 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 32.3
2013-01-11 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 31.4
2013-01-11 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 30.5
2013-01-11 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 29.6
2013-01-11 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 28.71
2013-01-11 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 27.81
2013-01-11 07:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 26.91
2013-01-11 08:00 | 10.97 | 1384.37 | 0 | 0 | 1395.34 | 26.01
2013-01-11 09:00 | 107.46 | 1287.88 | 0 | 0 | 1395.34 | 25.18
2013-01-11 10:00 | 86.51 | 1308.83 | 0 | 0 | 1395.34 | 24.34
2013-01-11 11:00 | 108.05 | 1287.29 | 0 | 0 | 1395.34 | 23.51
2013-01-11 12:00 | 112.48 | 1282.86 | 0 | 0 | 1395.34 | 22.68
2013-01-11 13:00 | 15.03 | 1380.31 | 0 | 0 | 1395.34 | 21.79
2013-01-11 14:00 | 172.01 | 1223.32 | 0 | 0 | 1395.34 | 21
2013-01-11 15:00 | 24.53 | 1370.81 | 0 | 0 | 1395.34 | 20.12
2013-01-11 16:00 | 37.68 | 1357.66 | 0 | 0 | 1395.34 | 19.25
2013-01-11 17:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 18.35
2013-01-11 18:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 17.45
2013-01-11 19:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 16.55
2013-01-11 20:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 15.65
2013-01-11 21:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 14.75
2013-01-11 22:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 13.85
2013-01-11 23:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 12.95
2013-01-12 00:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 12.05
2013-01-12 01:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 11.15
2013-01-12 02:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 10.25
2013-01-12 03:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 9.35
2013-01-12 04:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 8.45
2013-01-12 05:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 7.55
2013-01-12 06:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 6.65
2013-01-12 07:00 | 0 | 1395.34 | 0 | 0 | 1395.34 | 5.75
2013-01-12 08:00 | 10.73 | 1384.61 | 0 | 0 | 1395.34 | 4.86
2013-01-12 09:00 | 174.88 | 1220.46 | 0 | 0 | 1395.34 | 4.07
2013-01-12 10:00 | 369.31 | 1026.03 | 0 | 0 | 1395.34 | 3.41
2013-01-12 11:00 | 355.12 | 1040.22 | 0 | 0 | 1395.34 | 2.74
2013-01-12 12:00 | 699.02 | 696.32 | 0 | 0 | 1395.34 | 2.29
2013-01-12 13:00 | 552.71 | 842.62 | 0 | 0 | 1395.34 | 1.75
2013-01-12 14:00 | 453.67 | 941.67 | 0 | 0 | 1395.34 | 1.14
2013-01-12 15:00 | 425.24 | 970.1 | 0 | 0 | 1395.34 | 0.52
2013-01-12 16:00 | 107.55 | 801.74 | 0 | 0 | 1395.34 | 0
2013-01-12 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-12 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-12 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-12 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-12 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-12 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-12 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 08:00 | 141.19 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 09:00 | 486.37 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 10:00 | 125.81 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 11:00 | 224.27 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 12:00 | 74.56 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 13:00 | 230.02 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 14:00 | 173.58 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 15:00 | 59.61 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 16:00 | 78.84 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-13 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 08:00 | 6.69 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 09:00 | 136.91 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 10:00 | 150.27 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 11:00 | 179.78 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 12:00 | 169.94 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 13:00 | 87.4 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 14:00 | 85.28 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 15:00 | 31.62 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 16:00 | 12.49 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-14 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 08:00 | 8.42 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 09:00 | 5.07 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 10:00 | 85.9 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 11:00 | 47.42 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 12:00 | 40.68 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 13:00 | 91.91 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 14:00 | 113.59 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 15:00 | 27.68 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 16:00 | 26.35 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-15 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 08:00 | 5.65 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 09:00 | 87.11 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 10:00 | 113.51 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 11:00 | 70.75 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 12:00 | 44.91 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 13:00 | 44.97 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 14:00 | 38.39 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 15:00 | 11.31 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 16:00 | 51.47 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-16 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 08:00 | 32.41 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 09:00 | 202.21 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 10:00 | 176.12 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 11:00 | 411.07 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 12:00 | 115.86 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 13:00 | 69.41 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 14:00 | 79.53 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 15:00 | 51.21 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 16:00 | 26.54 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 17:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-17 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 08:00 | 236.02 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 09:00 | 583.08 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 10:00 | 829.15 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 11:00 | 969.01 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 12:00 | 1006.55 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 13:00 | 961.61 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 14:00 | 828.69 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 15:00 | 602.1 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 16:00 | 288.57 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 17:00 | 17.18 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-18 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 08:00 | 233.37 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 09:00 | 567.14 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 10:00 | 800.97 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 11:00 | 928.65 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 12:00 | 974.11 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 13:00 | 934.02 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 14:00 | 810.11 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 15:00 | 598.7 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 16:00 | 292.65 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 17:00 | 18.22 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-19 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 08:00 | 223.55 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 09:00 | 551.73 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 10:00 | 783.36 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 11:00 | 931.27 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 12:00 | 987.01 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 13:00 | 951.52 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 14:00 | 827.33 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 15:00 | 610.88 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 16:00 | 298.67 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 17:00 | 18.29 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-20 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 08:00 | 28.22 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 09:00 | 58.71 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 10:00 | 64.9 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 11:00 | 230.47 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 12:00 | 493.16 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 13:00 | 289.51 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 14:00 | 542.71 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 15:00 | 592.8 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 16:00 | 240.69 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 17:00 | 0.5 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-21 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 07:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 08:00 | 261.9 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 09:00 | 623.1 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 10:00 | 886.25 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 11:00 | 896.98 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 12:00 | 1098.35 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 13:00 | 1059.67 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 14:00 | 926.11 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 15:00 | 691.61 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 16:00 | 349.2 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 17:00 | 26.99 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-22 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 06:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 07:00 | 0 | 0 | 0 | 0 | 1396.01 | 0
2013-01-23 08:00 | 258.39 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 09:00 | 613.71 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 10:00 | 867.3 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 11:00 | 1011.39 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 12:00 | 866.21 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 13:00 | 597.77 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 14:00 | 384.54 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 15:00 | 349.2 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 16:00 | 184.98 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 17:00 | 4.42 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 18:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 19:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 20:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 21:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 22:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-23 23:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 00:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 01:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 02:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 03:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 04:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 05:00 | 0 | 0 | 0 | 0 | 1395.34 | 0
2013-01-24 06:00 | 0 | 0 | 0 | 0 | 1474.13 | 0
2013-01-24 07:00 | 0 | 0 | 0 | 0 | 1504.12 | 0
2013-01-24 08:00 | 173.63 | 0 | 0 | 0 | 1455.05 | 0
Summary
Total residual import (MWh): | 353557
Min SoC (%): | 0
Hours at 0% SoC: | 281
Max solar this window (MW): | 1098.3
Load this window (MW, flat): | 1504.1
Total curtailment this window (MWh): | 0