# Virginia Grid LP Model — Reference Document

Living document — updated each time a change is made to the LP model. Reflects the model as of 2026-08-16, following the DoD-direction fix, curtailment-cost correction, CVOW_MW correction, and the still-open simultaneous charge/discharge investigation (flagged in yellow below).

# Objective

Meet the requirements of the Virginia Clean Economy Act and Renewable Portfolio Standard in the Dominion Virginia Load Serving Entity with the lowest-cost SLCOE (system levelized cost of energy) configuration that satisfies every constraint simultaneously — the single joint optimum, not a sequence of separately-tuned pieces.

# Objective Function

Minimize total annualized cost:

CRF x (SolarCAPEX + SolarOM) x S_

+ CRF x NaPowerCAPEX x PNA_

+ (CRF x NaEnergyCAPEX + StorFOM% x NaEnergyCAPEX) x ENA_

+ (CRF x FeEnergyCAPEX + StorFOM% x FeEnergyCAPEX) x (1 - ResilienceTilt%) x EFE_

+ SUM over t of [

GasPrice(year) x g[t]

+ NaCyclingCost x nd[t]

+ FeCyclingCost x fd[t]

+ UnservedPenalty x unserved[t]

+ CurtailmentCost x curt[t]

+ (- ExportPrice x export[t])          <- diagnostic only, see Section 7

]

Per-unit cost terms:

- CRF (capital recovery factor) ≈ 0.06744 — standard annualization of CAPEX over asset life

- NaCyclingCost = NaEnergyCAPEX / (NaCycleLife x 0.80) — Sandia BESS Cycling Price Model methodology; NaCycleLife is time-varying: 10,000 cycles for deployments before 2035, 15,000 from 2035 on

- FeCyclingCost = FeEnergyCAPEX / (1,000 x 1.0) — Form Energy-specific cycle-life figure, 100% DoD (no restriction — iron-air chemistry is tolerant of deep discharge)

- CurtailmentCost = $100/MWh — corrected from an original $0.01, then $1.0; validated directly (Section 6) as the minimum level that drives full utilization of built storage capacity before curtailing

- ResilienceTilt% = 3% — deliberate, disclosed policy preference for iron-air (long-duration) within the confirmed near-cost-flat region between Na-ion and iron-air build sizes; a policy choice, not a market-cost claim

- UnservedPenalty = $100,000/MWh — large enough that the solver only allows unserved demand as an absolute last resort

- Export term: NOT part of the standing model (Section 7) — shown to illustrate the mechanism only; gated by include_export, defaulting to False. Confirmed via direct testing to cause real build-size distortion (solar/storage overbuild to run a near-continuous export business) even under the corrected $37.80/MWh price — the project's standing decision to exclude export from the LP's own cost-minimization remains correct.

# System of Equations

Five families of equality constraints link every hourly variable together and tie the year to the four build decisions. All hold exactly (not just approximately) at the solved optimum.

## A. Energy balance (one row per hour, 8,760 rows)

S_ x solar_cf[t] + g[t] + bd[t] - bc[t] + nd[t] - nc[t] + fd[t] - fc[t]

+ unserved[t] - curt[t] - export[t]  =  demand[t] - nuclear[t] - exist_solar[t] - CVOW_MW x wind_cf[t]

The right-hand side ("residual") is fixed input data for a given checkpoint; everything on the left is a decision the LP makes. This is the core physics constraint — every other rule in the model is layered on top of it.

## B. Bath County SoC dynamics (8,761 rows: 8,760 hourly + 1 closing)

bsoc[0] = 0.5 x BATH_MWH + 0.80 x bc[0] - bd[0]

bsoc[t] = bsoc[t-1] + 0.80 x bc[t] - bd[t]                    for t = 1..T-1

bsoc[T-1] = 0.5 x BATH_MWH                                    (closing/cyclic constraint)

## C. Na-ion SoC dynamics (8,761 rows)

nsoc[0] = 0.5 x ENA_ + 0.90 x nc[0] - nd[0]

nsoc[t] = nsoc[t-1] + 0.90 x nc[t] - nd[t]                    for t = 1..T-1

nsoc[T-1] = 0.5 x ENA_                                        (closing/cyclic constraint)

## D. Iron-air SoC dynamics (8,761 rows)

fsoc[0] = 0.5 x EFE_ + FE_RTE_CHARGE(year) x fc[0] - fd[0]

fsoc[t] = fsoc[t-1] + FE_RTE_CHARGE(year) x fc[t] - fd[t]     for t = 1..T-1

fsoc[T-1] = 0.5 x EFE_                                        (closing/cyclic constraint)

FE_RTE_CHARGE varies by checkpoint year (iron_air_rte(year)) — not a fixed constant like Bath's 0.80 or Na's 0.90.

## E. Cumulative gas tracking (8,760 rows)

gascum[0] = 0.001 x g[0]

gascum[t] = gascum[t-1] + 0.001 x g[t]                        for t = 1..T-1

Tracked in GWh (the 0.001 factor), not MWh — keeps this row's magnitude comparable to the rest of the problem for numerical conditioning; exists solely so the RPS constraint (see Inequality table below) can check one running total against the year's clean-energy requirement.

# Decision Variables

## Build variables (4 total — one decision each, for the whole checkpoint year)

| Variable | Represents |
| --- | --- |
| S_ | Solar nameplate build size (new-build utility solar, MW) |
| PNA_ | Sodium-ion battery power rating (MW) |
| ENA_ | Sodium-ion battery energy capacity (MWh) — paired with PNA_; duration = ENA_/PNA_ |
| EFE_ | Iron-air battery energy capacity (MWh) — no separate power variable; power rating derived from EFE_/100 (fixed 100-hour design duration), not independently chosen |

Note the asymmetry: Na-ion gets two independent decisions (power and energy — the LP can pick any duration); iron-air gets one (energy only, duration fixed at 100 hours by construction). Bath County is existing, fixed infrastructure (3,000 MW / 24,000 MWh) — never a build decision.

## Hourly variables (14 per hour x 8,760 hours = 122,640 total)

| Variable | Represents |
| --- | --- |
| g | Gas dispatch this hour (MW) |
| bc | Bath charging power this hour (MW) |
| bd | Bath discharging power this hour (MW) |
| bsoc | Bath state of charge this hour (MWh) |
| nc | Na-ion charging power this hour (MW) |
| nd | Na-ion discharging power this hour (MW) |
| nsoc | Na-ion state of charge this hour (MWh) |
| fc | Iron-air charging power this hour (MW) |
| fd | Iron-air discharging power this hour (MW) |
| fsoc | Iron-air state of charge this hour (MWh) |
| gascum | Cumulative gas dispatched, running total through this hour (GWh) — exists solely for the RPS constraint, not because gas needs hour-by-hour tracking beyond g |
| unserved | Demand not met this hour (MW) — should always be 0 in a feasible, well-built checkpoint |
| curt | Curtailed (wasted) generation this hour (MWh) |
| export | Energy sold to external market this hour (MWh) — NOT part of the standing model; bounded to exactly 0 unless include_export=True is explicitly set for a diagnostic test (see Section 7) |

# Equality Constraints (things that must hold exactly)

| # | Constraint | Rows | What it enforces | Equation |
| --- | --- | --- | --- | --- |
| A | Energy balance | 8,760 | Supply (solar+gas+net discharge, all 3 storage) + unserved − curtailment − export = residual demand every hour. The core physics constraint. | S_·cf[t]+g[t]+bd[t]-bc[t]+nd[t]-nc[t]+fd[t]-fc[t]+unserved[t]-curt[t]-export[t]=residual[t] |
| B | Bath SoC dynamics | 8,761 | Bath's charge level this hour = last hour's + (charge x 0.80 RTE) − discharge. Year must end at the same 50% starting level. | bsoc[t]=bsoc[t-1]+0.80·bc[t]-bd[t]; bsoc[0],bsoc[T-1]=0.5·BATH_MWH |
| C | Na-ion SoC dynamics | 8,761 | Same idea, 90% charge efficiency, tied to the ENA_ build size. | nsoc[t]=nsoc[t-1]+0.90·nc[t]-nd[t]; nsoc[0],nsoc[T-1]=0.5·ENA_ |
| D | Iron-air SoC dynamics | 8,761 | Same idea, year-specific RTE, tied to EFE_. | fsoc[t]=fsoc[t-1]+RTE(yr)·fc[t]-fd[t]; fsoc[0],fsoc[T-1]=0.5·EFE_ |
| E | Cumulative gas tracking | 8,760 | Running total of gas dispatched (GWh), purely so the RPS constraint can check one number against the year's clean-energy requirement. | gascum[t]=gascum[t-1]+0.001·g[t] |

# Inequality Constraints (things bounded, not fixed)

| # | Constraint | Rows | What it enforces | Equation |
| --- | --- | --- | --- | --- |
| — | Na power/SoC bounds | 4/hr (35,040) | Charge ≤ rated power, discharge ≤ rated power, SoC within [20%,100%] of built capacity (standard DoD convention, corrected 2026-08-16 from a backwards [0%,80%] implementation). | nc,nd≤PNA_; 0.20·ENA_≤nsoc≤ENA_ |
| — | Iron-air power/SoC bounds | 3/hr (26,280) | Same idea, 100% DoD (no restriction — chemistry tolerant of deep discharge). | fc,fd≤EFE_/100; fsoc≤EFE_ |
| — | Joint charge+discharge caps ⚠ | 3/hr (26,280) | CORRECTED (2026-08-16): only bounds the SUM of charge+discharge to rated power — does NOT prevent both being simultaneously large as long as their sum stays within the rating. Confirmed directly: at large PNA_, both sides can run substantially at once (e.g. nc=120,000 + nd=119,000, summing to exactly the rating) — a real, open gap, not a complete fix. Currently restored (was briefly removed as "redundant," which held only while a since-removed charging incentive was also present). | bc+bd≤BATH_MW; nc+nd≤PNA_; fc+fd≤EFE_/100 |
| — | Bath's daily cycle limit | 365 (1/day) | Total Bath discharge in any calendar day ≤ 24,000 MWh (one full cycle) — Bath's physical design basis, confirmed via DOE/PNNL source. | SUM(bd[t], t in day) ≤ BATH_MWH |
| — | RPS / gas allowance | 1 | Total gas over the year ≤ the allowed share of clean generation. This is the exact constraint where the BUILD_SCALE bug lived (fixed 2026-08-16). | gascum[T-1] ≤ k·(clean_const + BUILD_SCALE·S_·Σsolar_cf)/1000 |

Total: ~43,803 equality rows + ~87,690 inequality rows (with the joint constraint restored) ≈ 131,493 constraint rows against ~122,644 decision variables.

# Additional Factors (floors, starting values, and other disclosed assumptions)

## Storage SoC initial/closing condition

- init_soc_frac = 0.5 (50%), applied uniformly to Bath, Na-ion, and iron-air

- Sets BOTH the starting condition (hour 0) AND requires the SAME level be reached again at the year's last hour (a closing/cyclic constraint) — prevents the LP from artificially draining storage in the final hours or starting artificially full, either of which would understate real operating cost relative to a genuinely repeating annual cycle

- A disclosed modeling convention, not an independently researched or sourced figure — chosen because it is neutral, not because 50% specifically reflects documented real-world practice

## Na-ion Depth of Discharge (DoD)

- Usable range: [20%, 100%] of built ENA_ — standard industry convention ("80% DoD" = discharging FROM full DOWN TO 20% remaining, reserve at the bottom)

- CORRECTED 2026-08-16: was previously implemented backwards as [0%, 80%] (reserve at the top) — caught via a direct question, not independent review. Matters for a real reason: sourced cycle-life figures (10,000/15,000 cycles) were almost certainly measured under the standard [20%,100%] protocol

- Directly tested and confirmed: this restriction was NOT the cause of the under-utilization issue investigated separately (Section 6) — removing it entirely did not improve curtailment capture

## VCEA storage floors (Va. Code §56-585.5(E)), interpolated between explicit statutory milestones

| Year | Short-duration floor (MW) | Long-duration floor (MW) |
| --- | --- | --- |
| 2030 | 4,000 (exact milestone) | 0 (no requirement yet) |
| 2035 | 8,000 (interpolated) | 2,000 (exact milestone) |
| 2040 | 12,000 (interpolated) | 3,000 (interpolated) |
| 2044.5 | 15,600 (interpolated) | 3,900 (interpolated) |
| 2045 | 16,000 (exact milestone) | 4,000 (exact milestone) |

- Short-duration: interpolated between (2030, 4,000 MW) and (2045, 16,000 MW) — no interim statutory milestone exists; interpolation is this project's own reasonable choice for years between, not a statutory figure itself

- Long-duration: 0 MW before 2035 (first milestone IS 2035, unlike short-duration's 2030 start), interpolated between (2035, 2,000 MW) and (2045, 4,000 MW) thereafter

- Both floors enforced as hard lower bounds on the relevant build variable (PNA_ for short-duration; EFE_/100, converted to an MWh floor via the 100-hour duration, for long-duration) — previously, the long-duration floor was NOT enforced anywhere in the model at all

## PJM reserve margin (IRM = 17.7%)

- Hard constraint (not priced/soft), checked at the single peak-net-demand hour identified from an unconstrained solve, using each resource's actual hourly availability rather than a blended ELCC-style credit

- Applied only to the 2030 checkpoint in practice — at every later checkpoint, storage built for other economic reasons already exceeds the requirement, making the constraint non-binding

## Gas capacity cap

- Schedule B baseline (year-dependent: 9,362 MW through 2044, dropping to 1,860 MW at 2045 per VCEA's terminal capacity reduction) plus a fixed 2,862 MW pool of extended-life existing units

- Applied as a simple upper bound on g[t] each hour, not a separate constraint row

## Resilience tilt

- RESILIENCE_TILT_PCT = 3% — reduces iron-air's effective CAPEX in the objective only; the real, unadjusted FE_ENERGY_CAPEX is still used everywhere else (Assumptions tab, land-use calculations)

- Rationale: iron-air's 100-hour duration provides genuine multi-day resilience Na-ion cannot structurally match — a criterion the LP does not otherwise price, since it optimizes cost alone. Explicitly does NOT capture Na-ion's real grid-services/fast-response value, which argues in the opposite direction — a disclosed, one-directional policy choice

## Key corrected constants (this session)

| Constant | Old (wrong) value | Corrected value | Where |
| --- | --- | --- | --- |
| CVOW_MW | 2,535.0 MW | 2,587.2 MW | lp_model.py — real nameplate (176 x 14.7MW Siemens Gamesa turbines), not the SAM proxy-turbine-count figure. Correction had been applied to a duplicate constant in driver.py but never to the source used by the actual energy balance. |
| EXPORT_AVG_PRICE | $63.00/MWh | $37.80/MWh | lp_model.py — code had the intermediate, since-rejected value; Assumptions tab's own documented correction history was the source of truth. |
| Curtailment cost | $0.01, then $1.0/MWh | $100.0/MWh | lp_model.py objective — validated directly as the level needed to drive full utilization of built storage before curtailing. |
| Na-ion DoD range | [0%, 80%] (backwards) | [20%, 100%] (standard convention) | lp_model.py inequality constraints. |

# Open Items

- Simultaneous charge/discharge: the joint power constraint (restored) only bounds the SUM of charge+discharge, not true mutual exclusivity — confirmed directly that both can run substantially simultaneously as long as their sum stays within the rated power. A genuine fix needs either (a) a true complementarity constraint (nc[t]·nd[t]=0, requires binary variables / MILP), or (b) a cycling cost on BOTH charge and discharge, not just discharge. Neither has been implemented or tested yet.

- Solver instability: a charging incentive (-$2/MWh on nc/fc) was found to cause genuine non-reproducibility — three identical solves gave three different answers with it present, zero spread once removed. Removed permanently, but its removal is what reintroduced the simultaneous-dispatch gap above, so the two open items are linked.

- Export price shape: the "seasonally-varying" export price multiplier is a completely unpopulated placeholder (flat 1.0 for every season/hour) despite code comments describing a real derivation methodology. Not yet fixed.

- 2030/2035/2040 checkpoints have not been rerun with the current, complete set of fixes (DoD direction, curtailment cost, CVOW_MW, joint constraint restoration) — only 2045 reflects the current model.